Instructions for updating the firmware in the 255 controllers

- Save the update Winn file (typical VR02_074.exe) in the C:/program files/Danfoss/AKCess folder.   Save the code loader files into a new folder you create in the C:/program files/Danfoss folder (typical VR02_074.cmot). Save the boot loader code in the same folder(typical Boot4_4.mot)

- Look and listen for non-typical activity of the racks or HVAC.

- Connect a Cat5 crossover cable to the laptop Ethernet port and the ethernet port on the controller. (J3) Connect the Danfoss direct connect cable from the laptop serial port to the direct connection port on the outside of the AKC 255.

- Pull back existing database and save to laptop using a standard naming convention.   (The intent is to have an original backup if needed because once this file is updated to the newer version; it cannot be restored to a previous version.)

- Log off of controller once all programs are saved.

- Check each program for overrides and document.  To find override conditions follow this path: Main menu / Communications / I/O network / List Points. A uppercase “M” will be under the Value column indicating the override.

- The old files must be updated to the newer version (2.074). Select simulate in the AKA65 software and the file to upgrade (Saved under step 4 above). Under Win Versions select the newer version (2.074)   and then select “Run”. Once open then select “save database” under file options and rename with a unique name indicating this is the newer file.

- Turn off compressors during the update process for safety reasons.

- Open the AKC 255 code loader software on the laptop, and turn off the laptops wireless Internet connection.

- Remove the burg jumper (JP2) to allow update download.

- Press CPU reset switch  (SW2) to reset unit.

- Look on the AKC 255 display for the IP address.

- If the IP address is all zeros then press the shift button on the controller keypad and the reset switch again.

- Verify valid IP address on the controller screen.

- Verify that the laptop acquires an IP address.

- At the Danfoss code loader select “connect”. Status will display the boot code version and it will say connected.

- The “download” button will become active once you are connected.

- The first step is Boot Loader Code. Select the browse button and under file type select .MOT file and the version you wish to upgrade. This file is stored as indicated in step 1 above.  Select “Download” and the status bar will show the progress. This process should take approximately 20-30 seconds to complete, and the controller will automatically reset once complete.

- Once again select “Connect” on the code loader and then browse. Under file type select .CMOT file and the version to upgrade to, select “open”.

- Select “Download” and the status bar will indicate the download progress. This process will take about 3 minutes to complete.

- Reinstall the Burg jumper and press reset. (SW2)

- The AKC 255 screen will prompt to auto-convert this file. Select the 1 key on the AKC 255 keypad to accept. Verify the correct software version and boot loader from the main menu under “AK2-SC255 Info” screen.

- Reconnect to the controller via the AK65 software and get authorized at supervisor level. Select “load database” from the file menu and follow the on screen instructions to load the database that you upgraded in step 7.

- When finished uploading the new file turn back on all compressors and verify the operation of the rack and all I/O is online.

- Configure the history and start history collection.

- The update process is now complete.

# Text boxes

If a warning message pops up that says: “Setting have changed. Please reset the 255 and reconnect”. Then do just that. Reset SW2 and reconnect.