## 90KW @ 400V
Mains option : Disconnect
kW Rating : 90 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4230-0GA | 250A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX3557-3DA01 |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6083 |  | SIEMENS | 1
4 | -Q1 | CABLE LUGS | 9SG12 | CU 120qmm for M10 | KLAUKE | 3
5 | -Q1;-U1 | POWER CABLE | 4521016 | 120Sq mm Black | LAPP | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
11 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
12 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
13 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
14 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
15 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 110KW @ 400V
Mains option : Disconnect
kW Rating : 110 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4230-0GA | 250A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX3557-3DA01 |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6083 |  | SIEMENS | 1
4 | -Q1 | CABLE LUGS | 10SG10 | CU 150qmm for M10 | KLAUKE | 3
5 | -Q1;-U1 | POWER CABLE | 4521017 | 150Sq mm Black | LAPP | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
11 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
12 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
13 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
14 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
15 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 132KW @ 400V
Mains option : Disconnect
kW Rating : 132 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4330-0GA | 400A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX3557-3DA01 |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6083 |  | SIEMENS | 1
4 | -Q1 | CABLE LUGS | 11SG10 | CU 185qmm for M10 | KLAUKE | 3
5 | -Q1;-U1 | POWER CABLE | 4521018 | 185Sq mm Black | LAPP | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
11 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
12 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
13 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
14 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
15 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 160KW @ 400V
Mains option : Disconnect
kW Rating : 160 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4330-0GA | 400A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX3557-3DA01 |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6083 |  | SIEMENS | 1
4 | -Q1 | CABLE LUGS | 12SG10 | CU 240qmm for M10 | KLAUKE | 3
5 | -Q1;-U1 | POWER CABLE | 4521019 | 240Sq mm Black | LAPP | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
11 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
12 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
13 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
14 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
15 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 200KW @ 400V
Mains option : Disconnect
kW Rating : 200 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4330-0GA | 400A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX3557-3DA01 |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6083 |  | SIEMENS | 1
4 | -Q1;-U1 | FLEXIBAR-FIXING FS 24 | 553550 |  | ERICO | 3
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -Q1;-U1 | POWER CABLE | 552580 | FLEXIBAR 5x24x1 | ERICO | 6
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
15 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 250KW @ 400V
Mains option : Disconnect
kW Rating : 250 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4430-0GA | 630A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER upper, lower | 3KX2252-0C |  | SIEMENS | 1
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6084 |  | SIEMENS | 1
4 | -Q1;-U1 | FLEXIBAR-FIXING FS 24 | 553550 |  | ERICO | 3
5 | -Q1;-U1 | POWER CABLE | 552600 | FLEXIBAR 8x24x1 | ERICO | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
15 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 315KW @ 400V
Mains option : Disconnect
kW Rating : 315 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4430-0GA | 630A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX2252-0C |  | SIEMENS | 1
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6084 |  | SIEMENS | 1
4 | -Q1;-U1 | FLEXIBAR-FIXING FS 32 | 553560 |  | ERICO | 3
5 | -Q1;-U1 | POWER CABLE | 552660 | FLEXIBAR 6x32x1 | ERICO | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
15 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
16 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
17 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter
Note: Item 14 +15 required for frequency inverter devices Bg E2!

## 355KW @ 400V
Mains option : Disconnect
kW Rating : 355 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4530-0GA | 1000A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX2252-0C |  | SIEMENS | 6
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6084 |  | SIEMENS | 1
4 | -Q1;-U1 | FLEXIBAR-BEFESTIGUNG FS 40-63 | 553570 |  | ERICO | 3
5 | -Q1;-U1 | POWER CABLE | 552730 | FLEXIBAR 6x40x1 | ERICO | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
15 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
16 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
17 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter

## 400KW @ 400V
Mains option : Disconnect
kW Rating : 400 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -Q1 | DISCONNECTOR | 3KE4530-0GA | 1000A,TRIPLE POLE,35kA | SIEMENS | 1
2 | -Q1 | TERMINAL COVER | 3KX2252-0C |  | SIEMENS | 1
3 | -Q1 | EXTENSION SHAFT 600 MM | 8UC6084 |  | SIEMENS | 1
4 | -Q1;-U1 | FLEXIBAR-Fixation FS 40-63 | 553570 |  | ERICO | 3
5 | -Q1;-U1 | POWER CABLE | 552730 | FLEXIBAR 6x40x1 | ERICO | 6
6 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
7 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
8 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
9 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
15 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
16 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
17 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
all PE connections to be 50sqm for drive<=>PE busbar
Semiconductor fuses in the inverter