## 90KW @ 400V
Mains option : Contactor
kW Rating : 90 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1056-6AP36 | AC3, 185A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1956-4EA1 |  | SIEMENS | 2
3 | -C1 | CABLE LUGS | 9SG8 | CU 120qmm for M8 | KLAUKE | 3
4 | -C1;-U1 | POWER CABLE | 4521016 | 120Sq mm Black | LAPP | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
Pre-fuse (customer): 250A gG (VLT holds aR fuses)

## 110KW @ 400V
Mains option : Contactor
kW Rating : 110 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1064-6AP36 | AC3, 225A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1966-4EA1 |  | SIEMENS | 2
3 | -C1 | CABLE LUGS | 10SG10 | CU 150qmm for M10 | KLAUKE | 3
4 | -C1;-U1 | POWER CABLE | 4521017 | 150Sq mm Black | LAPP | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
Pre-fuse (customer): 250A gG (VLT holds aR fuses)

## 132KW @ 400V
Mains option : Contactor
kW Rating : 132 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
S.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1065-6AP36 | AC3, 265A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1966-4EA1 |  | SIEMENS | 2
3 | -C1 | CABLE LUGS | 11SG10 | CU 185qmm for M10 | KLAUKE | 3
4 | -C1;-U1 | POWER CABLE | 4521018 | 185Sq mm Black | LAPP | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
Pre-fuse (customer): 315A gG (VLT holds aR fuses)

## 160KW @ 400V
Mains option : Contactor
kW Rating : 160 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1066-6AP36 | AC3, 300A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1966-4EA1 |  | SIEMENS | 2
3 | -C1 | CABLE LUGS | 12SG10 | CU 240qmm for M10 | KLAUKE | 3
4 | -C1;-U1 | POWER CABLE | 4521019 | 240Sq mm Black | LAPP | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
10 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
11 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
12 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
13 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
14 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
Pre-fuse (customer): 350A gG (VLT holds aR fuses)

## 200KW @ 400V
Mains option : Contactor
kW Rating : 200 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1075-6AP36 | AC3, 400A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1966-4EA1 |  | SIEMENS | 2
3 | -C1;-U1 | FLEXIBAR-FIXING FS 24 | 553550 |  | ERICO | 3
4 | -C1;-U1 | POWER CABLE | 552580 | FLEXIBAR 5x24x1 | ERICO | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
10 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
11 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
12 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
13 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
14 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
Pre-fuse (customer): 450A gG (VLT holds aR fuses)

## 250KW @ 400V
Mains option : Contactor
kW Rating : 250 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR | 3RT1076-6AP36 | AC3, 500A, 400V AC, 3Pole, with 2NO+2NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3RT1966-4EA1 |  | SIEMENS | 2
3 | -C1;-U1 | FLEXIBAR-FIXING FS 24 | 553550 |  | ERICO | 3
4 | -C1;-U1 | POWER CABLE | 552600 | FLEXIBAR 8x24x1 | ERICO | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
10 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
11 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
12 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
13 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
14 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
Pre-fuse (customer): 500A gG (VLT holds aR fuses)

## 315KW @ 400V
Mains option : Contactor
kW Rating : 315 kW FU-Gehäuse E2
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR(W/O Surge Protection) | 3TF6844-0CM7-Z-A02 | AC3, 630A, 400V AC, 3Pole, with 3NO+3NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3TX7686-0A |  | SIEMENS | 2
3 | -C1;-U1 | FLEXIBAR-FIXING FS 32 | 553560 |  | ERICO | 3
4 | -C1;-U1 | POWER CABLE | 552660 | FLEXIBAR 6x32x1 | ERICO | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
10 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
11 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
12 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
13 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
14 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
15 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
16 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
Pre-fuse (customer): 630A gG (VLT holds aR fuses)

## 355KW @ 400V
Mains option : Contactor
kW Rating : 355 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR(W/O Surge Protection) | 3TF6944-0CM7-Z-A02 | AC3, 820A, 400V AC, 3Pole, with 3NO+3NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3TX7696-0A |  | SIEMENS | 2
3 | -C1;-U1 | FLEXIBAR-BEFESTIGUNG FS 40-63 | 553570 |  | ERICO | 3
4 | -C1;-U1 | POWER CABLE | 552730 | FLEXIBAR 6x40x1 | ERICO | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
10 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
11 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
12 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
13 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
14 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
15 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
16 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
Pre-fuse (customer): 800A gG (VLT holds aR fuses)

## 400KW @ 400V
Mains option : Contactor
kW Rating : 400 kW
Mains Voltage : 400 V AC
Control Voltage :24 V DC
SL.NO | DT | Designation | Part Number | Technical Data | Manufacturer | Qty
1 | -C1 | POWER CONTACTOR(W/O Surge Protection) | 3TF6944-0CM7-Z-A02 | AC3, 820A, 400V AC, 3Pole, with 3NO+3NC Auxiliary Contacts | SIEMENS | 1
2 | -C1 | TERMINAL COVER FOR RAILS CONNECTIONS | 3TX7696-0A |  | SIEMENS | 2
3 | -C1;-U1 | FLEXIBAR-Fixation FS 40-63 | 553570 |  | ERICO | 3
4 | -C1;-U1 | POWER CABLE | 552730 | FLEXIBAR 6x40x1 | ERICO | 6
5 | -U1 | PE CABLE | 4521003 | 50Sq mm Green/Yellow | LAPP | 1
6 | -K1;-K2 | AUXILIARY CONTACTOR | 3RH21 22-1BB40 | 2 NO+2 NC,COIL VOLTAGE : 24V DC | SIEMENS | 2
7 | -K1;-K2 | VARISTOR | 3RT2916-1BB00 | AC 24-48V, DC 24-70V | SIEMENS | 2
8 | -K1 | CONTROL CABLE | 4520011S | 1.5 Sq mm Black, H07V-K (X07V-K) | LAPP | 1
9 | -X1 | Feed-through terminal with spring-cage connection | ST 2,5 |  | PHOENIX | 4
10 | -X1 | Terminal strip marker carrier - KLM 3 | 0811969 |  | PHOENIX | 1
11 | -X1 | End clamp - CLIPFIX 35-5 | 3022276 |  | PHOENIX | 2
12 | -X1 | Protective conductor terminal with spring-cage connection | ST 2,5-PE |  | PHOENIX | 2
13 | -X1 | Lid D-ST 2,5 | 3030417 |  | PHOENIX | 1
14 | -U1 | copper connection latch | 28M14303A70 |  | ELOTEC | 3
15 | -U1 | FLEXIBAR-connection clamp FC 50x40 | 553040 |  | ERICO | 3
16 | -U1 | CABLE LUGS | 6R10 | CU 50qmm for M10 | KLAUKE | 1
Pre-fuse (customer): 800A gG (VLT holds aR fuses)