## Sheet1
FC102-C1-IP55, 18 to 55kW Version 1.0
VLT® FC 102 HVAC Drive BIM Manufacturer Specification
Danfoss Drives, Denmark, Tel. +45 7488 2222, WEB: WWW.drives.danfoss.com, E-mail: info@danfoss.com
Product
Manufacturer | Danfoss
Model | VLT® HVAC Drive
Description | Variable Frequency Drive for HVAC Applications
Product Type | FC-102 HVAC
Performance
Power supply and power rating | See information below
Supply Frequency | 50 Hz / 60 Hz + 10%
Overload torque | 110% for 1 minute every 10 minute
True power factor | > 0.9
Displacement power factor (cosø) | > 0.98 near unity
THiD | ~46% at short circuit ratio >120
Operating temperature range | -250 to 500C / -130 to 1220F
Power Cycle | 1-2 times / min.
Output data (U,V,W)
Output voltage | 0-100% of supply voltage
Output switching frequency | 2-16 kHz
Ramp time | 1-3600 sec.
Output frequency | 0-590 Hz
Power Cycle | 1-2 times / min.
Input data | Standard configuration
Digital input (Programmable) | 4 (0-24VDC, PNP/NPN)
Pulse input (Programmable) | 2 (0-24VDC, PNP 0,1-110kHz - can be programmed as digital output)
Analouge input | 2 (0-10V or 0/4-20mA - scaleable)
Output data | Standard configuration
Digital output (Programmable) | 2 (0-24VDC, PNP/NPN - can be programmed as input)
Relay output (Programmable) | 2 (240VAC, 2A / 400VAC, 2A)
Analouge output | 1 (0/4-20mA - scaleable)
Fieldbus Communication | Visit www.Danfoss.com for latest update
Standard built in (RS-485) | Options (Slot -A)
FC Protocol | BACnet MSTP - MCA 109
N2 Metasys | BACnet IP - MCA125
FLN Apogee | Ethernet/IP - MCA 121
Modbus RTU | DeviceNet - MCA 104
BACnet MSTP (embedded) | LonWorks - MCA 108
Modbus TCP - MCA 122
PROFIBUS DP - MCA 101 or PROFINET - MCA 120
Installation
IP / Nema rating | IP55 / Type 12
Mounting | Wall
Dimensions | Included in the Revit files
Max. motor cable length (screened) | 150m / 490 Feet (H1 RFI filter & EMC ClassA1/A2 & Category C2/C3)
Max. motor cable length (unscreened) | 300m / 980 Feet
Weight (kg) | 45kg / 99.2lb
Approvals
RFI Filter | IEC 61800-3, Category C1 / C2 / C3
EMC emission compliance | IEC 55011 Class A1/A2/B, IEC 61000-6-3/4, IEC 61800-3 Category C1/C2/C3
Harmonic compliance | IEC/EN 61000-3-12 for short circuit ratios > 120
Product Variants
Type Code | FC-102-P18K-T2-E55
Mains Supply (L1,L2,L3) | 200-240V AC -/+ 10%
Rated kW | 18kW / 25HP
Rated Continual Current (A) | 74.8 Amp
Type Code | FC-102-P22K-T2-E55
Mains Supply (L1,L2,L3) | 200-240V AC -/+ 10%
Rated kW | 22kW / 30HP
Rated Continual Current (A) | 88 Amp
Type Code | FC-102-P30K-T2-E55
Mains Supply (L1,L2,L3) | 200-240V AC -/+ 10%
Rated kW | 30kW / 40HP
Rated Continual Current (A) | 115 Amp
Type Code | FC-102-P37K-T4-E55
Mains Supply (L1,L2,L3) | 380-480V AC -/+ 10%
Rated kW | 37kW / 50HP
Rated Continual Current (A) | 73 Amp (380-440V) / 65 Amp (441-480V)
Type Code | FC-102-P37K-T6-E55
Mains Supply (L1,L2,L3) | 525-600V AC -/+ 10%
Rated kW | 37kW / 50HP
Rated Continual Current (A) | 83 Amp
Type Code | FC-102-P45K-T4-E55
Mains Supply (L1,L2,L3) | 380-480V AC -/+ 10%
Rated kW | 45kW / 60HP
Rated Continual Current (A) | 90 Amp (380-440V) / 80 Amp (441-480V)
Type Code | FC-102-P45K-T6-E55
Mains Supply (L1,L2,L3) | 525-600V AC -/+ 10%
Rated kW | 45kW / 60HP
Rated Continual Current (A) | 62 Amp
Type Code | FC-102-P55K-T4-E55
Mains Supply (L1,L2,L3) | 380-480V AC -/+ 10%
Rated kW | 55kW / 75HP
Rated Continual Current (A) | 106 Amp (380-440V) / 105 Amp (441-480V)
Type Code | FC-102-P55K-T6-E55
Mains Supply (L1,L2,L3) | 525-600V AC -/+ 10%
Rated kW | 55kW / 75HP
Rated Continual Current (A) | 83 Amp