## Sheet1
Its system integrator responcibility to get correct grid code settings from the transmission company.
[6 empty] | NXPV200 | NXPV200 | NXPV200 or newer | NXPV200 or newer
[6 empty] | ARFIF106_V103 | ARFIF106_V103 | ARFIF106 V104 or newer | ARFIF106 V104 or newer
[8 empty] | TCR High Voltage | TCR Medium Voltage
ID | Index | Variable Text | Default | Unit | Format | UL California | UL Hawaii | VDE-AR-N 4120:2018-11 | VDE-AR-N 4110:2018-11
3201 | P 2.17.1 | GGC License | 0 |  | 60
3254 | P 2.17.2 | Set Grid Code | 0 / No Action
3250 | P 2.17.3 | EnableGridCode | 0 / Disabled |  |  | 2 /Enabled | 2 /Enabled | 2 /Enabled | 2 /Enabled
| G 2.17.5 | Anti-Islanding
3324 | P 2.17.4 | Anti-islanding | 0 / Disabled |  |  | 1 / Active | 1 / Active | 1 / Active | 1 / Active
3404 | P 2.17.4.2 | High Volt AI | 0 | % | 62
3405 | P 2.17.4.3 | Low Volt AI | 0 | % | 62
3406 | P 2.17.4.4 | High Freq AI | 110 | % | 62
3407 | P 2.17.4.5 | Low Freq. AI | 80 | % | 62 | 65 | 65
3408 | P 2.17.4.6 | AI Trip Delay | 50 | ms | 60
3426 | P 2.17.4.7 | AntiIslanding Kp | 0 | % | 60
| G 2.17.5 | FRT
3251 | P 2.17.5.1 | FRT Function | 0 / Disab;Both |  |  | 1 / Enab; Limits | 1 / Enab; Limits | 1 / Enab; Limits | 1 / Enab; Limits
3252 | P 2.17.5.2 | ReactivInjection | 0 / Tri:N, Bi:N |  |  | 2 / Tru:Y, Bi:N | 2 / Tru:Y, Bi:N | 1 / Tri:Y, Bi:Y | 1 / Tri:Y, Bi:Y
3323 | P 2.17.5.3 | Symmet.Reactive | 1 / Yes
| G 2.17.6 | ReConnection
3253 | P 2.17.6.1 | ReConnectTime | 2 | s | 103 | 300 | 300 | 600 | 600
3255 | P 2.17.6.2 | ReConnTimeStop | 2 | s | 103 | 300 | 300 | 600 | 600
3297 | P 2.17.6.3 | ReConRampUpRate | 20 | %/s | 62 | 2 | 0.33 | 0.5 | 0.5
3421 | P 2.17.6.4 | RampReleaseDelay | 600 | ms | 60
| G 2.17.7 | Line Voltage
3364 | P 2.17.7.1 | VoltageMonitor | 1 / PhaseMinMax |  |  | 0 / Average | 0 / Average | 1 / PhaseMinMax | 1 / PhaseMinMax
3256 | P 2.17.7.2 | LV High 1 | 115 | % | 62 | 115 | 115 | 125 | 125
3257 | P 2.17.7.3 | LV High 1 Delay | 50 | ms | 100 | 12500 | 1000 | 100 | 100
3412 | P 2.17.7.4 | LV High 1 Plim | 300 | % | 61 | 5 | 5
3258 | P 2.17.7.5 | LV High 2 | 0 | % | 62 | 120 | 122
3259 | P 2.17.7.6 | LV High 2 Delay | 0 | ms | 100 | 160 | 160
3413 | P 2.17.7.7 | LV High 2 Plim | 300 | % | 61
3361 | P 2.17.7.8 | LV High 3 | 0 | % | 62
3362 | P 2.17.7.9 | LV High 3 Delay | 0 | ms | 100
3363 | P 2.17.7.10 | LV High 3 PLim | 300 | % | 61
3260 | P 2.17.7.11 | LV Low 1 | 0 | % | 62 | 85 | 85 | 80 | 80
3261 | P 2.17.7.12 | LV Low 1 Delay | 0 | ms | 100 | 20500 | 20500 | 2100 | 2100
3414 | P 2.17.7.13 | LV Low 1 Plim | 300 | % | 60
3262 | P 2.17.7.14 | LV Low 2 | 80 | % | 62 | 60 | 60 | 30 | 30
3263 | P 2.17.7.15 | LV Low 2 Delay | 50 | ms | 100 | 10500 | 12000 | 800 | 800
3415 | P 2.17.7.16 | LV Low 2 Plim | 300 | % | 60
3365 | P 2.17.7.17 | LV Low 3 | 0 | % | 62 | 50 | 50
3366 | P 2.17.7.18 | LV Low 3 Delay | 0 | ms | 100 | 1250 | 1900
3367 | P 2.17.7.19 | LV Low 3 PLim | 300 | % | 61 | 5 | 5
3416 | P 2.17.7.20 | LV Low 4 | 0 | % | 62
3417 | P 2.17.7.21 | LV Low Delay | 160 | ms | 100
3418 | P 2.17.7.22 | LV Low Plim | 300 | % | 61
3353 | P 2.17.7.23 | 10MinAveHighVolt | 0 | % | 62
3376 | P 2.17.7.24 | 10minAvTripDelay | 50 | ms | 100
3410 | P 2.17.7.25 | VoltageResponceTime | 0 | ms | 60 | 110 | 110
3376 | P 2.17.7.26 | Plim Down Rate | 100 | %/s | 60
| G 2.17.8 | Line Frequency
3423 | P 2.17.8.1 | FrequencyMonitor | 0 / Normal |  |  | 1 / FastShort | 1 / FastShort | 1 / FastShort | 1 / FastShort
3264 | P 2.17.8.2 | LF High 1 | 103 | % | 62 | 105 | 108.5 | 105 | 105
3265 | P 2.17.8.3 | LF High 1 Delay | 50 | ms | 100 | 160 | 160 | 50 | 50
3266 | P 2.17.8.4 | LF High 2 | 0 | % | 62 | 101.66 | 106.66 | 103 | 103
3267 | P 2.17.8.5 | LF High 2 Delay | 0 | ms | 100 | 299800 | 20300 | 4500 | 4500
3368 | P 2.17.8.6 | LF High 3 | 0 | % | 62
3369 | P 2.17.8.7 | LF High 3 Delay | 0 | ms | 100
3268 | P 2.17.8.8 | LF Low 1 | 0 | % | 62 | 95.83 | 93.33
3269 | P 2.17.8.9 | LF Low 1 Delay | 0 | ms | 100 | 299800 | 20300
3270 | P 2.17.8.10 | LF Low 2 | 95 | % | 62 | 93.33 | 83.16 | 95 | 95
3271 | P 2.17.8.11 | LF Low 2 Delay | 50 | ms | 100 | 160 | 160 | 50 | 50
3370 | P 2.17.8.12 | LF Low 3 | 0 | % | 62
3371 | P 2.17.8.13 | LF Low 3 Delay | 0 | ms | 1000
3322 | P 2.17.8.14 | LF MaxChangeRate | 2.5 | Hz/s | 62 | 2.5 | 2.5
3399 | P 2.17.8.15 | FreqResponseTime | 0 | ms | 60 | 130 | 130
3411 | P 2.17.8.16 | TOffCycles | 2 | x | 60 | 3 | 3
| G 2.17.9 | Volt. Time Trip
3272 | P 2.17.9.1 | Voltage X0 | 0 | % | 102
3273 | P 2.17.9.2 | Time Y0 | 0 | ms | 100
3274 | P 2.17.9.3 | Voltage X1 | 0 | % | 102
3275 | P 2.17.9.4 | Time Y1 | 0 | ms | 100
3276 | P 2.17.9.5 | Voltage X2 | 0 | % | 102
3277 | P 2.17.9.6 | Time Y2 | 0 | ms | 100
3278 | P 2.17.9.7 | Voltage X3 | 0 | % | 102
3279 | P 2.17.9.8 | Time Y3 | 0 | ms | 100
3280 | P 2.17.9.9 | Voltage X4 | 0 | % | 102
3281 | P 2.17.9.10 | Time Y4 | 0 | ms | 100
3282 | P 2.17.9.11 | Voltage X5 | 0 | % | 102
3283 | P 2.17.9.12 | Time Y5 | 0 | ms | 100
3284 | P 2.17.9.13 | Voltage X6 | 0 | % | 102
3285 | P 2.17.9.14 | Time Y6 | 0 | ms | 100
| G 2.17.10 | Line OK Lim
3287 | P 2.17.10.1 | LF OK High | 0 | % | 62 | 100.83 | 105 | 100.2 | 100.2
3286 | P 2.17.10.2 | LF OK Low | 0 | % | 62 | 97.5 | 95 | 99.8 | 99.8
3289 | P 2.17.10.3 | LV OK High | 0 | % | 62 | 110 | 110 | 110 | 110
3288 | P 2.17.10.4 | LV OK Low | 0 | % | 62 | 88 | 88 | 95 | 95
3290 | P 2.17.10.5 | Line OK Delay | 0 | ms | 100 | 200 | 200 | 200 | 200
| G 2.17.11 | ReactivInjection | [5 empty] | Defined by network operator | Defined by network operator
3314 | P 2.17.11.1 | UV Reactive Mode | 0 / Linear |  |  |  |  | Defined by network operator | Defined by network operator
3377 | P 2.17.11.2 | OV Reactive Mode | 0 / Linear |  |  |  |  | Defined by network operator | Defined by network operator
| G 2.17.11.3 | Linear UV | [5 empty] | Defined by network operator | Defined by network operator
3291 | P 2.17.11.3.1 | UV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3292 | P 2.17.11.3.2 | UV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3293 | P 2.17.11.3.3 | UV Reac.MaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3294 | P 2.17.11.3.4 | UV Bi Reac. Ref | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.11.4 | Linear OV | [5 empty] | Defined by network operator | Defined by network operator
3300 | P 2.17.11.4.1 | OV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3301 | P 2.17.11.4.2 | OV Max Reactiv | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3302 | P 2.17.11.4.3 | OV React Slope | 0 | %/% | 62 |  |  | Defined by network operator | Defined by network operator
3303 | P 2.17.11.4.4 | OV React PLim In | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3329 | P 2.17.11.4.5 | OV React PLimOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.11.5 | PowerLock UV | [5 empty] | Defined by network operator | Defined by network operator
3315 | P 2.17.11.5.1 | UV PowerLockIn | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3316 | P 2.17.11.5.2 | UV PowerLockOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3372 | P 2.17.11.5.3 | UV PowrLogInMode | 0 / VoltLevlTrig |  |  |  |  | Defined by network operator | Defined by network operator
3291 | P 2.17.11.5.4 | UV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3292 | P 2.17.11.5.5 | UV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3317 | P 2.17.11.5.6 | UV LockOutVoltag | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3318 | P 2.17.11.5.7 | UV ReacHalfRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3293 | P 2.17.11.5.8 | UV Reac.MaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3294 | P 2.17.11.5.9 | UV Bi ReacMaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.11.6 | PowerLock OV | [5 empty] | Defined by network operator | Defined by network operator
3378 | P 2.17.11.6.1 | OV PowerLockIn | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3379 | P 2.17.11.6.2 | OV PowerLockOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3380 | P 2.17.11.6.3 | OV PowrLogInMode | 0 / VoltLevlTrig |  |  |  |  | Defined by network operator | Defined by network operator
3300 | P 2.17.11.6.4 | OV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3320 | P 2.17.11.6.5 | OV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3319 | P 2.17.11.6.6 | OV LockOutVoltag | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3321 | P 2.17.11.6.7 | OV ReacHalfRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3301 | P 2.17.11.6.8 | OV Max Reactiv | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.11.7 | Q U Power | [5 empty] | Defined by network operator | Defined by network operator
3341 | P 2.17.11.7.1 | HighMax Q Power | 0 | % | 61 | 30 | 44 | Defined by network operator | Defined by network operator
3340 | P 2.17.11.7.2 | HighMaxVoltage | 115 | % | 62 | 107 | 106 | Defined by network operator | Defined by network operator
3339 | P 2.17.11.7.3 | HighMinVoltage | 105 | % | 62 | 103.3 | 103 | Defined by network operator | Defined by network operator
3343 | P 2.17.11.7.5 | LowMaxVoltage | 90 | % | 62 | 96.7 | 97 | Defined by network operator | Defined by network operator
3342 | P 2.17.11.7.6 | LowMinVoltage | 80 | % | 62 | 92 | 94 | Defined by network operator | Defined by network operator
3344 | P 2.17.11.7.4 | LowMax Q Power | 0 | % | 61 | -30 | -44 | Defined by network operator | Defined by network operator
| G 2.17.11.8 | Q U Curve | [5 empty] | Defined by network operator | Defined by network operator
3385 | P 2.17.11.8.1 | Voltage 01 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3391 | P 2.17.11.8.2 | Q Power 01 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3386 | P 2.17.11.8.3 | Voltage 02 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3392 | P 2.17.11.8.4 | Q Power 02 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3387 | P 2.17.11.8.5 | Voltage 03 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3393 | P 2.17.11.8.6 | Q Power 03 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3388 | P 2.17.11.8.7 | Voltage 04 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3394 | P 2.17.11.8.8 | Q Power 04 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3389 | P 2.17.11.8.9 | Voltage 05 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3395 | P 2.17.11.8.10 | Q Power 05 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3390 | P 2.17.11.8.11 | Voltage 06 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3396 | P 2.17.11.8.12 | Q Power 06 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.12 | Power Limit Ref
| G2.17.12.1 | General
3324 | P 2.17.12.1.1 | PowerRampUp | 50 | %/s | 62 | 100 | 100 | 0.5 | 0.5
3397 | P 2.17.12.1.2 | GC Max Power | 105 | % | 61
| G 2.17.12.2 | High Freq
3307 | P 2.17.12.2.1 | HighFreqModes | 0 / High Limit
3295 | P 2.17.12.2.2 | HighFreqLowCornr | 0 | % | 62 | 100.16 | 100.06 | 100.4 | 100.4
3239 | P 2.17.12.2.3 | HighFreqPLimSlop | 50 | %/Hz | 61 | 50 | 41.7 | 100 | 100
3308 | P 2.17.12.2.4 | HighFreqLockOut | 0 | % | 62
3298 | P 2.17.12.2.5 | HighFreqPLimRamp | -1 | %/s | 62
3299 | P 2.17.12.2.6 | HighFreqPReleDel | 50 | ms | 100
3374 | P 2.17.12.2.7 | HighLFFullPRelDe | 0 | ms | 100
3402 | P 2.17.12.2.8 | HighFreqLimOnDel | 100 | ms | 60
3296 | P 2.17.12.2.9 | HighFreqHigCornr | 0 | % | 62
3309 | P 2.17.12.2.10 | HighFreqPowRatio | 0 | % | 61
| G 2.17.12.3 | High Voltage
3360 | P 2.17.12.3.1 | Limit Mode | 0 / High Limit
3325 | P 2.17.12.3.2 | LogInVoltage | 0 | % | 62 |  | 106
3326 | P 2.17.12.3.3 | LogOutVoltage | 0 | % | 62
3327 | P 2.17.12.3.4 | Limit Slope | 0 | %/% | 61 |  | 25
3424 | P 2.17.12.3.5 | PLimReleaseDelay | 1000 | ms | 60
3425 | P 2.17.12.3.6 | PLimRelRampRate | -0.01 | %/s | 62
| G 2.17.12.4 | LowVoltChargeLim
3347 | P 2.17.12.4.1 | PChargeMaxVolt | 0 | % | 62
3348 | P 2.17.12.4.2 | PChargeMinVolt | 0 | % | 62
| G2.17.12.5 | LowFreqCharge
3354 | P 2.17.12.5.1 | PChargeLimMode | 1 / Minimum
3349 | P 2.17.12.5.2 | PChargeMaxFreq | 0 | % | 62
3350 | P 2.17.12.5.3 | PChargeMinFreq | 0 | % | 62
3351 | P 2.17.12.5.4 | PChargLogOutFreq | 0 | % | 62
3352 | P 2.17.12.5.5 | PChrgLogOutDelay | 50 | ms | 100
3355 | P 2.17.12.5.6 | PCharRelPRate | 50 | %/s | 62
3403 | P 2.17.12.5.7 | PChargeOnDelay | 50 | ms | 60
| G 2.17.12.6 | LowFreqPowerIncr
3334 | P 2.17.12.6.1 | PowerIncHighFreq | 0 | % | 62 | 99.83 |  | 99.6 | 99.6
3335 | P 2.17.12.6.2 | PowerIncSlope | 0 | %/% | 61 | 50 |  | 200 | 200
3336 | P 2.17.12.6.3 | PowerInc Max | 0 | % | 61 | 100
| G 2.17.13 | CosPhiiControl
3345 | P 2.17.13.1 | CosPhiiMode | 0 / Direct Ref
3304 | P 2.17.13.2 | CosPhiiRef | 0 |  | 63 |  | -0.95
| G 2.17.13.3 | VoltageLogInOut
3305 | P 2.17.13.3.1 | LockInVoltage | 0 | % | 62
3306 | P 2.17.13.3.2 | LockOutVoltage | 0 | % | 62
3346 | P 2.17.13.3.3 | MaxCosRef | 1 |  | 63
| G2.17 13 4 | Act. Current
3357 | P 2.17.13.4.1 | MinCosRefMinPowr | 15 | % | 61
3356 | P 2.17.13.4.2 | MinCosRef | 1 |  | 63
3358 | P 2.17.13.4.3 | CosRefMidPower | 50 | % | 61
3359 | P 2.17.13.4.4 | MaxCosRefMaxPowr | 150 | % | 61
3346 | P 2.17.13.4.5 | MaxCosRef | 1 |  | 63
| G 2.17.14 | External In
3310 | P 2.17.14.1 | Ext GC Trip NO | DigIN:0.1 |  | 1
3398 | P 2.17.14.2 | Ext GC Trip NC | DigIN:0.2 |  | 1
3311 | P 2.17.14.3 | SeparateFLimMon | DigIN:0.1 |  | 1
3312 | P 2.17.14.4 | SepFreqHighLim | 0 | % | 62
3313 | P 2.17.14.5 | SepFreqLowLim | 0 | % | 62
| G 2.17.15 | Options
3328 | P 2.17.15.1 | GC Options 1 | 0 |  | 60
3332 | P 2.17.15.2 | Voltage Filt TC | 20 | ms | 60
3333 | P 2.17.15.3 | Frequecy Filt TC | 35 | ms | 60
3400 | P 2.17.15.4 | FRT Opt | 0 |  | 60 | 8 | 8
3337 | P 2.17.15.5 | Vac Stop Offset | 0 | % | 62
3338 | P 2.17.15.6 | Vac Run Offset | 0 | % | 62
1529 | P 2.17.15.7 | PowerFoll.Hyst. | 3 | % | 61
3373 | P 2.17.15.8 | LVHighFiltTC | 100 | ms | 60 | 150 | 150
3375 | P 2.17.15.9 | LineFreqLow TC | 20 | ms | 60 | 25 | 25
3382 | P 2.17.15.10 | FRT Trig Level | 0 | % | 62
3409 | P 2.17.15.11 | Current x TC | 16 | ms | 60
3420 | P 2.17.15.12 | LV Feedback Kp | 0 | % | 62 | 100 | 100
3422 | P 2.17.15.13 | Current Priority | 0 / Normal |  |  | 4 / CosPhii&Reac | 4 / CosPhii&Reac