## Grid Code parameters
Its system integrator responcibility to get correct grid code settings from the transmission company.
[6 empty] | NXPV200 | NXPV200 | NXPV200+ | NXPV200+
[6 empty] | ARFIF106 V103 | ARFIF106 V103 | ARFIF106 Vxxx | ARFIF106 Vxxx
[8 empty] | TCR High Voltage | TCR Medium Voltage
ID | Index | Variable Text | Default | Unit | Format | UL California | UL Hawaii | VDE-AR-N 4120:2018-11 | VDE-AR-N 4110:2018-11 | Italy
3201 | P 2.17.1 | GGC License | 0 |  | 60
3254 | P 2.17.2 | Set Grid Code | 0 / No Action
3250 | P 2.17.3 | EnableGridCode | 0 / Disabled |  |  | 2 /Enabled | 2 /Enabled | 2 /Enabled | 2 /Enabled
| G 2.17.4 | Anti-Islanding
3324 | P 2.17.4.1 | Anti-islanding | 0 / Disabled |  |  | 1 / Active | 1 / Active | 1 / Active | 1 / Active
3404 | P 2.17.4.2 | High Volt AI | 0 | % | 62
3405 | P 2.17.4.3 | Low Volt AI | 0 | % | 62
3406 | P 2.17.4.4 | High Freq AI | 110 | % | 62
3407 | P 2.17.4.5 | Low Freq. AI | 80 | % | 62 | 65 | 65
3408 | P 2.17.4.6 | AI Trip Delay | 50 | ms | 60
3426 | P 2.17.4.7 | AntiIslanding Kp | 0 | % | 60 | 1000 | 1000
| G 2.17.5 | FRT
3251 | P 2.17.5.1 | FRT Function | 0 / Disab;Both |  |  | 1 / Enab; Limits | 1 / Enab; Limits | 1 / Enab; Limits | 1 / Enab; Limits | 1 / Enab; Limits
3252 | P 2.17.5.2 | ReactivInjection | 0 / Tri:N, Bi:N |  |  | 2 / Tru:Y, Bi:N | 2 / Tru:Y, Bi:N | 1 / Tri:Y, Bi:Y | 1 / Tri:Y, Bi:Y | 1 / TriY, BiY
3323 | P 2.17.5.3 | Symmet.Reactive | 1 / Yes
| G 2.17.5.4 | FRT Timer
3284 | P 2.17.5.4.1 | Voltage X6 | 0 | % | 102
3285 | P 2.17.5.4.2 | Time Y6 | 0 | ms | 100
3282 | P 2.17.5.4.3 | Voltage X5 | 0 | % | 102
3283 | P 2.17.5.4.4 | Time Y5 | 0 | ms | 100
3280 | P 2.17.5.4.5 | Voltage X4 | 0 | % | 102
3281 | P 2.17.5.4.6 | Time Y4 | 0 | ms | 100
3278 | P 2.17.5.4.7 | Voltage X3 | 0 | % | 102
3279 | P 2.17.5.4.8 | Time Y3 | 0 | ms | 100
3276 | P 2.17.5.4.9 | Voltage X2 | 0 | % | 102
3277 | P 2.17.5.4.10 | Time Y2 | 0 | ms | 100
3274 | P 2.17.5.4.11 | Voltage X1 | 0 | % | 102
3275 | P 2.17.5.4.12 | Time Y1 | 0 | ms | 100
3272 | P 2.17.5.4.13 | Voltage X0 | 0 | % | 102
3273 | P 2.17.5.4.14 | Time Y0 | 0 | ms | 100
| G 2.17.6 | ReConnection
3253 | P 2.17.6.1 | ReConnectTime | 2 | s | 103 | 300 | 300 | 600 | 600
3255 | P 2.17.6.2 | ReConnTimeStop | 2 | s | 103 | 300 | 300 | 600 | 600
3297 | P 2.17.6.3 | ReConRampUpRate | 20 | %/s | 62 | 2 | 0.33 | 0.5 | 0.5
3421 | P 2.17.6.4 | RampReleaseDelay | 600 | ms | 60
3287 | P 2.17.6.5 | LF OK High | 0 | % | 62 | 100.83 | 105 | 100.2 | 100.2
3286 | P 2.17.6.6 | LF OK Low | 0 | % | 62 | 97.5 | 95 | 99.8 | 99.8
3289 | P 2.17.6.7 | LV OK High | 0 | % | 62 | 110 | 110 | 110 | 110
3288 | P 2.17.6.8 | LV OK Low | 0 | % | 62 | 88 | 88 | 95 | 95
3290 | P 2.17.6.9 | Line OK Delay | 0 | ms | 100 | 200 | 200 | 200 | 200
| G 2.17.7 | Line Voltage
3364 | P 2.17.7.1 | VoltageMonitor | 1 / PhaseMinMax |  |  | 0 / Average | 0 / Average | 1 / PhaseMinMax | 1 / PhaseMinMax
3256 | P 2.17.7.2 | LV High 1 | 115 | % | 62 | 115 | 115 | 125 | 125 | 120
3257 | P 2.17.7.3 | LV High 1 Delay | 50 | ms | 100 | 12500 | 1000 | 100 | 100 | 100
3412 | P 2.17.7.4 | LV High 1 Plim | 300 | % | 61 | 5 | 5
3258 | P 2.17.7.5 | LV High 2 | 0 | % | 62 | 120 | 122 |  |  | 115
3259 | P 2.17.7.6 | LV High 2 Delay | 0 | ms | 100 | 160 | 160 |  |  | 1000
3413 | P 2.17.7.7 | LV High 2 Plim | 300 | % | 61
3361 | P 2.17.7.8 | LV High 3 | 0 | % | 62 |  |  |  |  | 110
3362 | P 2.17.7.9 | LV High 3 Delay | 0 | ms | 100 |  |  |  |  | 60000
3363 | P 2.17.7.10 | LV High 3 PLim | 300 | % | 61
3260 | P 2.17.7.11 | LV Low 1 | 0 | % | 62 | 85 | 85 | 80 | 80 | 90
3261 | P 2.17.7.12 | LV Low 1 Delay | 0 | ms | 100 | 20500 | 20500 | 2100 | 2100 | 60000
3414 | P 2.17.7.13 | LV Low 1 Plim | 300 | % | 60
3262 | P 2.17.7.14 | LV Low 2 | 80 | % | 62 | 60 | 60 | 30 | 30 | 85
3263 | P 2.17.7.15 | LV Low 2 Delay | 50 | ms | 100 | 10500 | 12000 | 800 | 800 | 2000
3415 | P 2.17.7.16 | LV Low 2 Plim | 300 | % | 60
3365 | P 2.17.7.17 | LV Low 3 | 0 | % | 62 | 50 | 50 |  |  | 30
3366 | P 2.17.7.18 | LV Low 3 Delay | 0 | ms | 100 | 1250 | 1900 |  |  | 850
3367 | P 2.17.7.19 | LV Low 3 PLim | 300 | % | 61 | 5 | 5
3416 | P 2.17.7.20 | LV Low 4 | 0 | % | 62
3417 | P 2.17.7.21 | LV Low Delay | 160 | ms | 100
3418 | P 2.17.7.22 | LV Low Plim | 300 | % | 61
3353 | P 2.17.7.23 | 10MinAveHighVolt | 0 | % | 62
3376 | P 2.17.7.24 | 10minAvTripDelay | 50 | ms | 100
3410 | P 2.17.7.25 | VoltageResponceTime | 0 | ms | 60 | 110 | 110 |  |  | 110
3376 | P 2.17.7.26 | Plim Down Rate | 100 | %/s | 60
| G 2.17.8 | Line Frequency
3423 | P 2.17.8.1 | FrequencyMonitor | 0 / Normal |  |  | 1 / FastShort | 1 / FastShort | 1 / FastShort | 1 / FastShort
3264 | P 2.17.8.2 | LF High 1 | 103 | % | 62 | 105 | 108.5 | 105 | 105 | 105
3265 | P 2.17.8.3 | LF High 1 Delay | 50 | ms | 100 | 160 | 160 | 50 | 50 | 100
3266 | P 2.17.8.4 | LF High 2 | 0 | % | 62 | 101.66 | 106.66 | 103 | 103 | 103
3267 | P 2.17.8.5 | LF High 2 Delay | 0 | ms | 100 | 299800 | 20300 | 4500 | 4500 | 1000
3368 | P 2.17.8.6 | LF High 3 | 0 | % | 62
3369 | P 2.17.8.7 | LF High 3 Delay | 0 | ms | 100
3268 | P 2.17.8.8 | LF Low 1 | 0 | % | 62 | 95.83 | 93.33 |  |  | 95
3269 | P 2.17.8.9 | LF Low 1 Delay | 0 | ms | 100 | 299800 | 20300 |  |  | 4000
3270 | P 2.17.8.10 | LF Low 2 | 95 | % | 62 | 93.33 | 83.16 | 95 | 95 | 93
3271 | P 2.17.8.11 | LF Low 2 Delay | 50 | ms | 100 | 160 | 160 | 50 | 50 | 100
3370 | P 2.17.8.12 | LF Low 3 | 0 | % | 62
3371 | P 2.17.8.13 | LF Low 3 Delay | 0 | ms | 1000
3322 | P 2.17.8.14 | LF MaxChangeRate | 2.5 | Hz/s | 62 | 2.5 | 2.5
3399 | P 2.17.8.15 | FreqResponseTime | 0 | ms | 60 | 130 | 130 |  |  | 130
3411 | P 2.17.8.16 | TOffCycles | 2 | x | 60 | 3 | 3
| G 2.17.9 | ReactiveCurrent
3314 | P 2.17.9.1 | UV Reactive Mode | 0 / Linear |  |  |  |  | Defined by network operator | Defined by network operator | 1 / PowerLock
3377 | P 2.17.9.2 | OV Reactive Mode | 0 / Linear |  |  |  |  | Defined by network operator | Defined by network operator | 1 / PowerLock
| G 2.17.9.3 | Linear UV
3291 | P 2.17.9.3.1 | UV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3292 | P 2.17.9.3.2 | UV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3293 | P 2.17.9.3.3 | UV Reac.MaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3294 | P 2.17.9.3.4 | UV Bi Reac. Ref | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.9.4 | Linear OV
3300 | P 2.17.9.4.1 | OV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3301 | P 2.17.9.4.2 | OV Max Reactiv | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3302 | P 2.17.9.4.3 | OV React Slope | 0 | %/% | 62 |  |  | Defined by network operator | Defined by network operator
3303 | P 2.17.9.4.4 | OV React PLim In | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3329 | P 2.17.9.4.5 | OV React PLimOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.9.5 | PowerLock UV
3315 | P 2.17.9.5.1 | UV PowerLockIn | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 25
3316 | P 2.17.9.5.2 | UV PowerLockOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 7.5
3372 | P 2.17.9.5.3 | UV PowrLogInMode | 0 / VoltLevlTrig |  |  |  |  | Defined by network operator | Defined by network operator
3291 | P 2.17.9.5.4 | UV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 92
3292 | P 2.17.9.5.5 | UV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 90
3317 | P 2.17.9.5.6 | UV LockOutVoltag | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 95
3318 | P 2.17.9.5.7 | UV ReacHalfRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 24.2
3293 | P 2.17.9.5.8 | UV Reac.MaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 48.3
3294 | P 2.17.9.5.9 | UV Bi ReacMaxRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 48.3
3444 | P 2.17.9.5.10 | UV Reac.Start V | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
| G 2.17.9.6 | PowerLock OV
3378 | P 2.17.9.6.1 | OV PowerLockIn | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 25
3379 | P 2.17.9.6.2 | OV PowerLockOut | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 7.5
3380 | P 2.17.9.6.3 | OV PowrLogInMode | 0 / VoltLevlTrig |  |  |  |  | Defined by network operator | Defined by network operator
3300 | P 2.17.9.6.4 | OV Low Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 108
3320 | P 2.17.9.6.5 | OV High Corner | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 110
3319 | P 2.17.9.6.6 | OV LockOutVoltag | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator | 105
3321 | P 2.17.9.6.7 | OV ReacHalfRef | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 24.2
3301 | P 2.17.9.6.8 | OV Max Reactiv | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator | 48.3
3445 | P 2.17.9.6.9 | OV Reac.Start V | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
| G 2.17.9.7 | DynamicSupport
3501 | P 2.17.9.8.1 | OV Low Corner | 0 | % | 62
3502 | P 2.17.9.8.2 | UV High Corner | 0 | % | 62
3504 | P 2.17.9.8.3 | PosSeqSlope | 2 | %/% | 62
3505 | P 2.17.9.8.4 | NegSeqSlope | 2 | %/% | 62
3503 | P 2.17.9.8.5 | SlopeMaxReactive | 100 | % | 61
3506 | P 2.17.9.8.6 | SudPosChanLim | 10 | % | 62
3507 | P 2.17.9.8.7 | SudNegChanLim | 10 | % | 62
3508 | P 2.17.9.8.8 | RampZeroTime | 5 | s | 62
3509 | P 2.17.9.8.9 | ResetHysteresis | 1.5 | % | 62
3510 | P 2.17.9.8.10 | SuddebOffDelay | 5 | s | 63
| G 2.17.10 | ReactivePower
| G 2.17.10.1 | Q U Power
3341 | P 2.17.10.1.1 | HighMax Q Power | 0 | % | 61 | 30 | 44 | Defined by network operator | Defined by network operator
3340 | P 2.17.10.1.2 | HighMaxVoltage | 115 | % | 62 | 107 | 106 | Defined by network operator | Defined by network operator
3339 | P 2.17.10.1.3 | HighMinVoltage | 105 | % | 62 | 103.3 | 103 | Defined by network operator | Defined by network operator
3343 | P 2.17.10.1.4 | LowMaxVoltage | 90 | % | 62 | 96.7 | 97 | Defined by network operator | Defined by network operator
3342 | P 2.17.10.1.5 | LowMinVoltage | 80 | % | 62 | 92 | 94 | Defined by network operator | Defined by network operator
3344 | P 2.17.10.1.6 | LowMax Q Power | 0 | % | 61 | -30 | -44 | Defined by network operator | Defined by network operator
| G 2.17.10.2 | Q U Curve
3385 | P 2.17.10.2.1 | Voltage 01 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3391 | P 2.17.10.2.2 | Q Power 01 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3386 | P 2.17.10.2.3 | Voltage 02 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3392 | P 2.17.10.2.4 | Q Power 02 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3387 | P 2.17.10.2.5 | Voltage 03 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3393 | P 2.17.10.2.6 | Q Power 03 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3388 | P 2.17.10.2.7 | Voltage 04 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3394 | P 2.17.10.2.8 | Q Power 04 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3389 | P 2.17.10.2.9 | Voltage 05 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3395 | P 2.17.10.2.10 | Q Power 05 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
3390 | P 2.17.10.2.11 | Voltage 06 | 0 | % | 62 |  |  | Defined by network operator | Defined by network operator
3396 | P 2.17.10.2.12 | Q Power 06 | 0 | % | 61 |  |  | Defined by network operator | Defined by network operator
| G 2.17.10.3 | Q P Curve
3520 | P 2.17.10.3.1 | Power 01 | 0 | % | 61
3530 | P 2.17.10.3.2 | QP Power 01 | 0 | % | 61
3521 | P 2.17.10.3.3 | Power 02 | 0 | % | 61
3531 | P 2.17.10.3.4 | QP Power 02 | 0 | % | 61
3522 | P 2.17.10.3.5 | Power 03 | 0 | % | 61
3532 | P 2.17.10.3.6 | QP Power 03 | 0 | % | 61
3523 | P 2.17.10.3.7 | Power 04 | 0 | % | 61
3533 | P 2.17.10.3.8 | QP Power 04 | 0 | % | 61
3524 | P 2.17.10.3.9 | Power 05 | 0 | % | 61
3534 | P 2.17.10.3.10 | QP Power 05 | 0 | % | 61
3525 | P 2.17.10.3.11 | Power 06 | 0 | % | 61
3535 | P 2.17.10.3.12 | QP Power 06 | 0 | % | 61
3526 | P 2.17.10.3.13 | Power 07 | 0 | % | 61
3536 | P 2.17.10.3.14 | QP Power 07 | 0 | % | 61
3527 | P 2.17.10.3.15 | Power 08 | 0 | % | 61
3537 | P 2.17.10.3.16 | QP Power 08 | 0 | % | 61
3528 | P 2.17.10.3.17 | Power 09 | 0 | % | 61
3538 | P 2.17.10.3.18 | QP Power 09 | 0 | % | 61
3529 | P 2.17.10.3.19 | Power 10 | 0 | % | 61
3539 | P 2.17.10.3.20 | QP Power 10 | 0 | % | 61
| G 2.17.11 | Power Limit
| G2.17.11.1 | General
3324 | P 2.17.11.1.1 | PowerRampUp | 50 | %/s | 62 | 100 | 100 | 0.5 | 0.5
3397 | P 2.17.11.1.2 | GC Max Power | 105 | % | 61
3439 | P 2.17.11.1.3 | GC Min Power | 105 | % | 61
3449 | P 2.17.11.1.4 | PowerRefRamp | 50 | %/s | 62
| G 2.17.11.2 | HighFreqPowerLimit
3307 | P 2.17.11.2.1 | HighFreqModes | 0 / High Limit
3295 | P 2.17.11.2.2 | HighFreqLowCornr | 0 | % | 62 | 100.16 | 100.06 | 100.4 | 100.4
3239 | P 2.17.11.2.3 | HighFreqPLimSlop | 50 | %/Hz | 61 | 50 | 41.7 | 100 | 100
3308 | P 2.17.11.2.4 | HighFreqLockOut | 0 | % | 62
3298 | P 2.17.11.2.5 | HighFreqPLimRamp | -1 | %/s | 62
3299 | P 2.17.11.2.6 | HighFreqPReleDel | 50 | ms | 100
3374 | P 2.17.11.2.7 | HighLFFullPRelDe | 0 | ms | 100
3402 | P 2.17.11.2.8 | HighFreqLimOnDel | 100 | ms | 60
3296 | P 2.17.11.2.9 | HighFreqHigCornr | 0 | % | 62
3309 | P 2.17.11.2.10 | HighFreqPowRatio | 0 | % | 61
| G 2.17.11.3 | HighVoltPowerLimit
3360 | P 2.17.11.3.1 | Limit Mode | 0 / High Limit
3325 | P 2.17.11.3.2 | LogInVoltage | 0 | % | 62 |  | 106
3326 | P 2.17.11.3.3 | LogOutVoltage | 0 | % | 62
3327 | P 2.17.11.3.4 | Limit Slope | 0 | %/% | 61 |  | 25
3424 | P 2.17.11.3.5 | PLimReleaseDelay | 1000 | ms | 60
3425 | P 2.17.11.3.6 | PLimRelRampRate | -0.01 | %/s | 62
| G 2.17.11.4 | LowVoltChargeLimLimit
3347 | P 2.17.11.4.1 | PChargeMaxVolt | 0 | % | 62
3348 | P 2.17.11.4.2 | PChargeMinVolt | 0 | % | 62
| G2.17.11.5 | LowFreqChargeLimit
3354 | P 2.17.11.5.1 | PChargeLimMode | 1 / Minimum
3349 | P 2.17.11.5.2 | PChargeMaxFreq | 0 | % | 62
3350 | P 2.17.11.5.3 | PChargeMinFreq | 0 | % | 62
3351 | P 2.17.11.5.4 | PChargLogOutFreq | 0 | % | 62
3352 | P 2.17.11.5.5 | PChrgLogOutDelay | 50 | ms | 100
3355 | P 2.17.11.5.6 | PCharRelPRate | 50 | %/s | 62
3403 | P 2.17.11.5.7 | PChargeOnDelay | 50 | ms | 60
| G 2.17.12 | Power Reference
| G 2.17.12.1 | LowFreqPowerRef
3334 | P 2.17.12.1.1 | PowIncLogInFreq | 0 | % | 62 | 99.83 |  | 99.6 | 99.6
3437 | P 2.17.12.1.2 | PowIncLogOffFreq | 0 | % | 62
3335 | P 2.17.12.1.3 | PowerIncSlope | 0 | %/% | 61 | 50 |  | 200 | 200
3427 | P 2.17.12.1.4 | PowerIncOffRamp | -1 | %/s | 62
3438 | P 2.17.12.1.5 | PowerIncOffDelay | 0 | s | 103
3336 | P 2.17.12.1.6 | PowerInc Max | 300 | % | 61 | 100
3441 | P 2.17.12.1.7 | PowerIncLowFreq | 0 | % | 62
3443 | P 2.17.12.1.8 | PowerIncSetPRef | 0 | % | 62
| G 2.17.12.2 | HighFreqPowerRef
3428 | P 2.17.12.2.1 | PowDecLogInFreq | 0 | % | 62
3436 | P 2.17.12.2.2 | PowDecLogOffFreq | 0 | % | 62
3429 | P 2.17.12.2.3 | PowerDecSlope | 0 | %/% | 61
3431 | P 2.17.12.2.4 | PowerDecOffRamp | -1 | %/s | 62
3435 | P 2.17.12.2.5 | PowerDecOffDelay | 0 | s | 103
3430 | P 2.17.12.2.6 | PowerDec Max | -300 | % | 61
3442 | P 2.17.12.2.7 | PowerDecHighFreq | 0 | % | 62
| G 2.17.12.3 | HighVoltPowerRef
3432 | P 2.17.12.3.1 | HVPrefLowVol | 0 | %
3433 | P 2.17.12.3.2 | HV Power Ref | 0 | %
3434 | P 2.17.12.3.3 | HV Power Ramp | -1 | %/s
| G 2.17.13 | CosPhiiControl
3345 | P 2.17.13.1 | CosPhiiMode | 0 / Direct Ref
3304 | P 2.17.13.2 | CosPhiiRef | 0 |  | 63 |  | -0.95
| G 2.17.13.3 | VoltageLogInOut
3305 | P 2.17.13.3.1 | LockInVoltage | 0 | % | 62
3306 | P 2.17.13.3.2 | LockOutVoltage | 0 | % | 62
3346 | P 2.17.13.3.3 | MaxCosRef | 1 |  | 63
| G 2.17.13.4 | Act. Current
3357 | P 2.17.13.4.1 | MinCosRefMinPowr | 15 | % | 61
3356 | P 2.17.13.4.2 | MinCosRef | 1 |  | 63
3358 | P 2.17.13.4.3 | CosRefMidPower | 50 | % | 61
3359 | P 2.17.13.4.4 | MaxCosRefMaxPowr | 150 | % | 61
3346 | P 2.17.13.4.5 | MaxCosRef | 1 |  | 63
| G 2.17.14 | External In
3310 | P 2.17.14.1 | Ext GC Trip NO | DigIN:0.1 |  | 1
3398 | P 2.17.14.2 | Ext GC Trip NC | DigIN:0.2 |  | 1
3311 | P 2.17.14.3 | SeparateFLimMon | DigIN:0.1 |  | 1
3312 | P 2.17.14.4 | SepFreqHighLim | 0 | % | 62
3313 | P 2.17.14.5 | SepFreqLowLim | 0 | % | 62
| G 2.17.15 | LimitedGridSuppr
3446 | P 2.17.15.1 | EnableLimSup | DigIN:0.1 |  | 1
3447 | P 2.17.15.2 | LimitedSuppMode | 0 / Disabled
3448 | P 2.17.15.3 | VoltageLevel | 70 | % | 62
| G 2.17.16 | Options
3328 | P 2.17.16.1 | GC Options 1 | 0 |  | 60
3332 | P 2.17.16.2 | Voltage Filt TC | 20 | ms | 60
3333 | P 2.17.16.3 | Frequecy Filt TC | 35 | ms | 60
3400 | P 2.17.16.4 | FRT Opt | 0 |  | 60 | 8 | 8
3337 | P 2.17.16.5 | Vac Stop Offset | 0 | % | 62
3338 | P 2.17.16.6 | Vac Run Offset | 0 | % | 62
1529 | P 2.17.16.7 | PowerFoll.Hyst. | 3 | % | 61
3373 | P 2.17.16.8 | LVHighFiltTC | 100 | ms | 60 | 150 | 150
3375 | P 2.17.16.9 | LineFreqLow TC | 20 | ms | 60 | 25 | 25
3382 | P 2.17.16.10 | FRT Trig Level | 0 | % | 62
3409 | P 2.17.16.11 | Current x TC | 16 | ms | 60
3420 | P 2.17.16.12 | LV Feedback Kp | 0 | % | 62 | 100 | 100
3422 | P 2.17.16.13 | Current Priority | 0 / Normal |  |  | 4 / CosPhii&Reac | 4 / CosPhii&Reac
3441 | P 2.17.16.14 | LineFreqHigh TC | 120 | ms | 60
3540 | P 2.17.16.15 | ReactiveVoltComp | 0 / No
Other useful paramters to change or consider
1532 | P 2.1.2 | Grid Nom. Freq | 50 | Hz | 62 | 50 / 60
107 | P 2.6.1.1 | Current Limit | Varies | A | Varies | +25 %
1812 | P 2.6.2.5 | StopPowrRampRate | -0.01 | %/s | 62 | 50
620 | P 2.2.3.1 | DC Drooping | 0 | % | 62 | 1

## Drive Parameters
ID | Index | Variable Text | Value (Default) | Format In Use | Unit | Min | Max | Type | Format
110 | P 2.1.1 | Grid Nom Voltage | 400 | 60 | V | 100 | 625 | UINT | 60
1532 | P 2.1.2 | Grid Nom. Freq. | 50 | 62 | Hz | -320 | 320 | INT | 62
113 | P 2.1.3 | SystemRatedCurre | 385 | 60 | A | 0 | 693 | UINT | CurrentFormat
120 | P 2.1.4 | System Cos Phi | 0.85 | 32 |  | 0.3 | 1 | UINT | 32
213 | P 2.1.5 | SystemRated kVA | 0 | 60 | kVA | 0 | 32000 | UINT | UnitNomPowerFormat
116 | P 2.1.6 | SystemRated kW | 0 | 60 | kW | 0 | 32700 | UINT | UnitNomPowerFormat
1805 | P 2.1.7 | System Nom. DC | 675 | 60 |  | 0 | 1300 | UINT | 60
1501 | P 2.1.8 | Parallel AFE | 0 / Single |  |  | 0 | 1 | BOOL
1850 | P 2.1.9 | Transf. GC Side | 1000 | 61 | V | 0 | 3200 | INT | 61
1851 | P 2.1.10 | Transf.Grid Side | 1000 | 61 | V | 0 | 3200 | INT | 61
1852 | P 2.1.11 | Transf.PhaseShif | 0 | 61 | Deg | -360 | 360 | INT | 61
631 | P 2.1.12 | Identification | 0 / No Action |  |  | 0 | 1 | INT
1462 | P 2.2.1 | DC Voltage Ref | 110 | 62 | % | 105 | 320 | INT | 62
1459 | P 2.2.2 | Reactive CurrRef | 0 | 61 | % | -170 | 170 | INT | 61
620 | P 2.2.3.1 | DC Drooping | 0 | 52 | % | 0 | 100 | INT | 52
1199 | P 2.2.3.2 | DCV RefRampRate | 50 | 60 | %/s | -10 | 10000 | INT | 60
1678 | P 2.2.3.3 | DCV PIPoFollRate | 0.5 | 63 | % | -1 | 32 | INT | 63
1776 | P 2.2.3.4 | DC Ref Offset | 0 | 62 | % | -15 | 15 | INT | 62
1718 | P 2.2.3.5 | DC Ref Mode | 1 / Floating |  |  | 1 | 2 | INT
1791 | P 2.2.4.1 | FreqDroopOffset | 0 | 62 | Hz | -5 | 5 | INT | 62
417 | P 2.2.4.2 | Freq Down | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
418 | P 2.2.4.3 | Freq Up | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
331 | P 2.2.4.4 | FreqAdjustRate | 0.1 | 53 | Hz/s | 0.001 | 20 | UINT | 53
1558 | P 2.2.4.5 | Freq. Max Adjust | 2.5 | 62 | Hz | 0 | 25 | INT | 62
1533 | P 2.2.4.6 | BaseCurrent Ref. | 0 | 61 | % | -170 | 170 | INT | 61
1536 | P 2.2.4.7 | BaseRefRampRate | 100 | 60 | %/s | -10000 | 10000 | INT | 60
1537 | P 2.2.4.8 | BaseRefToZero | 0 / No Action |  |  | 0 | 10 | INT
1538 | P 2.2.4.9 | BaseRefAtStop | 5 | 61 | % | 0 | 170 | INT | 61
367 | P 2.2.4.10 | FreqMotPotReset | 0 / No Action |  |  | 0 | 3 | INT
1914 | P 2.2.4.11 | ReferenceMode | 0 / Pure Iq Ref |  |  | 0 | 1 | INT
1905 | P 2.2.4.12.1 | PID Power Act. | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1911 | P 2.2.4.12.2 | PID Kp Power | 120 | 102 | % | 0 | 10000 | DINT | 102
1906 | P 2.2.4.12.3 | PID Ti Power | 210 | 100 | ms | 0 | 100000 | DINT | 100
1903 | P 2.2.4.12.4 | PID DC Low | -5 | 62 | % | -50 | 50 | INT | 62
1904 | P 2.2.4.12.5 | PID DC High | 5 | 62 | % | -50 | 50 | INT | 62
1810 | P 2.2.4.12.6 | Ref Down Rate | 50 | 62 | %/s | -1 | 320 | INT | PowerRefRampFormat
1811 | P 2.2.4.12.7 | Ref Up Rate | 50 | 62 | %/s | -1 | 320 | INT | PowerRefRampFormat
1842 | P 2.2.4.12.8 | PI LimHystToRef | 5 | 61 | % | -20 | 20 | INT | 61
1844 | P 2.2.4.12.9 | PI RefHystToLim | 2 | 61 | % | -20 | 20 | INT | 61
1843 | P 2.2.4.12.10 | ZeroErrorLimit | 0 | 61 | % | 0 | 20 | INT | 61
1845 | P 2.2.4.12.11 | PI StartDelay | 200 | 60 | ms | 0 | 32000 | INT | 60
1915 | P 2.2.4.12.12 | PID FRT Kp | 300 | 102 | % | 0 | 1000 | DINT | 102
1916 | P 2.2.4.12.13 | PID FRT Ti | 125 | 100 | ms | 0 | 100000 | DINT | 100
4530 | P 2.2.4.12.14 | RefRampFormat | 3 / #,## |  |  | 1 | 3 | INT
4510 | P 2.2.4.13.1 | PowDecLogInFreq | 0 | 62 | % | 0 | 200 | INT | 62
4511 | P 2.2.4.13.2 | PowDecLogOffFreq | 0 | 62 | % | 0 | 200 | INT | 62
4512 | P 2.2.4.13.3 | PowerDecSlope | 0 | 61 | %/% | 0 | 200 | INT | 61
4513 | P 2.2.4.13.4 | PowerDecOffRamp | -1 | 62 | %/s | -1 | 320 | INT | 62
4514 | P 2.2.4.13.5 | PowerDecOffDelay | 0 | 103 | s | 0 | 600 | DINT | 103
4515 | P 2.2.4.13.6 | PowerDec Max | -300 | 61 | % | -300 | 300 | INT | 61
4516 | P 2.2.4.13.7 | PowerDecHighFreq | 0 | 62 | % | 0 | 200 | INT | 62
4517 | P 2.2.4.14.1 | PowIncLogInFreq | 0 | 62 | % | 0 | 200 | INT | 62
4518 | P 2.2.4.14.2 | PowIncLogOffFreq | 0 | 62 | % | 0 | 200 | INT | 62
4519 | P 2.2.4.14.3 | PowerIncSlope | 0 | 61 | %/% | 0 | 200 | INT | 61
4520 | P 2.2.4.14.4 | PowerIncOffRamp | -1 | 62 | %/s | -1 | 320 | INT | 62
4521 | P 2.2.4.14.5 | PowerIncOffDelay | 0 | 103 | s | 0 | 600 | DINT | 103
4522 | P 2.2.4.14.6 | PowerInc Max | 300 | 61 | % | -300 | 300 | INT | 61
4523 | P 2.2.4.14.7 | PowerIncLowFreq | 0 | 62 | % | 0 | 200 | INT | 62
4524 | P 2.2.4.14.8 | PowerIncSetPFreq | 0 | 62 | % | 0 | 200 | INT | 62
1557 | P 2.2.5.1 | Reactive Rate | 1 | 61 | %/s | 0 | 1000 | INT | 61
1553 | P 2.2.5.2 | Reactive Up | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1554 | P 2.2.5.3 | Reactive Down | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1559 | P 2.2.5.4 | MaxReactivAdjust | 25 | 61 | % | -100 | 100 | INT | 61
1644 | P 2.2.5.5 | ReactMotPotReset | 1 / At Stop |  |  | 0 | 1 | INT
603 | P 2.2.6.1 | Voltage at FWP | 100 | 52 | % | 10 | 200 | UINT | 52
602 | P 2.2.6.2 | Field WeakngPnt | 45 | 62 | Hz | 6 | 320 | UINT | FreqFormat
1790 | P 2.2.6.3 | VoltgeCorrection | 0 | 60 | V | -50 | 50 | INT | 60
1460 | P 2.2.6.4 | Capacitor Size | 6.8 | 41 | % | 0 | 100 | INT | 41
1461 | P 2.2.6.5 | Inductor Size | 1.2 | 41 | % | 0 | 100 | INT | 41
1465 | P 2.2.6.6 | Inductor Losses | 12 | 41 | % | 0 | 100 | INT | 41
1551 | P 2.2.6.7 | Voltage Down | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1550 | P 2.2.6.8 | Voltage Up | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1555 | P 2.2.6.9 | Voltage Rate | 0.1 | 63 | %/s | 0 | 10 | INT | 63
1639 | P 2.2.6.10 | VoltageMaxAdjust | 10 | 62 | % | 0 | 20 | INT | 62
1640 | P 2.2.6.11 | VoltMotPotReset | 0 / No Action |  |  | 0 | 4 | INT
1641 | P 2.2.6.12 | StartVoltageMode | 1 / Drooping |  |  | 0 | 3 | INT
1642 | P 2.2.6.13 | ResetZeroQDelay | 0 | 62 | s | 0 | 120 | INT | 62
1643 | P 2.2.6.14 | ZeroQMaxAdjust | 7.5 | 62 |  | 0 | 50 | INT | 62
3330 | P 2.2.6.15 | CapacitorSize2nd | 0 | 61 | % | 0 | 100 | INT | 61
3331 | P 2.2.6.16 | CapSize2ndVoltag | 0 | 61 | V | 0 | 1100 | INT | 61
103 | P 2.3.1 | Ramp Time | 25 | 61 | s | 0.1 | 3200 | INT | 61
1980 | P 2.3.2 | Ramp Range | 50 | 62 | Hz | 0.05 | 100 | UINT | 62
300 | P 2.4.1.1 | Start/Stop Logic | 0 / Start-No Act |  |  | 0 | 3 | INT
1091 | P 2.4.1.2 | Input Inversion | 4 | 60 |  | 0 | 65535 | UINT | 60
4001 | P 2.4.1.3 | IOStopDelToggle | 15 | 62 | s | 0 | 320 | INT | 62
4000 | P 2.4.1.4 | IOStarDelToggle | 15 | 62 | s | 0 | 320 | INT | 62
403 | P 2.4.2.1 | Start Signal 1 | DigIN:A.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
404 | P 2.4.2.2 | Start Signal 2 | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1600 | P 2.4.2.3 | Open MCB | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1453 | P 2.4.2.4 | MCB Feedback | DigIN:A.4 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
414 | P 2.4.2.5 | Fault Reset | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
405 | P 2.4.2.6 | Ext Fault 1 | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
406 | P 2.4.2.7 | Ext Fault 2 | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
407 | P 2.4.2.8 | Run Enable | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1602 | P 2.4.2.9 | NET Synhronizt. | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1705 | P 2.4.2.10 | NET CloseEnable | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1604 | P 2.4.2.11 | NET CloseRequest | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1660 | P 2.4.2.12 | NET CB | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1540 | P 2.4.2.13 | Forced AFE Mode | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
750 | P 2.4.2.14 | Cooling Monitor | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1708 | P 2.4.2.15 | Use MCB 2 | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1710 | P 2.4.2.16 | MCB2 Feedback | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1711 | P 2.4.2.17 | AFE Mode 2 | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1712 | P 2.4.2.18 | AFE Mode 3 | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1213 | P 2.4.2.19 | Quick Stop | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1179 | P 2.4.2.20 | LCL Temperature | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1896 | P 2.4.2.21 | RR Enable | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
409 | P 2.4.2.22 | I/O Term Control | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
410 | P 2.4.2.23 | Keypad Control | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
411 | P 2.4.2.24 | Fieldbus Control | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1619 | P 2.4.2.25 | Enable MCB Close | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1608 | P 2.4.2.26 | Reset P/Hz MPot | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
441 | P 2.4.2.27 | DC Ground Fault | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
377 | P 2.4.3.1 | AI1 Signal Sel | AnIN:0.1 | 3 |  | AnIN:0.1 | AnIN:E.10 | INT | 3
324 | P 2.4.3.2 | AI1 Filter Time | 0 | 53 | s | 0 | 32 | INT | 53
321 | P 2.4.3.3 | AI1 Custom Min | 0 | 62 | % | -160 | 160 | INT | 62
322 | P 2.4.3.4 | AI1 Custom Max | 100 | 62 | % | -160 | 160 | INT | 62
387 | P 2.4.3.5 | AI1 Signal Inv | 0 / No Inversion |  |  | 0 | 1 | BOOL
303 | P 2.4.3.6 | AI1 Scale Min | 0 | 60 |  | -32000 | 32000 | INT | 60
304 | P 2.4.3.7 | AI1 Scale Max | 0 | 60 |  | -32000 | 32000 | INT | 60
1507 | P 2.4.3.8 | AI1 Controll. ID | 0 | 60 |  | 0 | 10000 | UINT | 60
388 | P 2.4.4.1 | AI2 Signal Sel | AnIN:0.1 | 3 |  | AnIN:0.1 | AnIN:E.10 | INT | 3
329 | P 2.4.4.2 | AI2 Filter Time | 0 | 53 | s | 0 | 32 | INT | 53
326 | P 2.4.4.3 | AI2 Custom Min | 20 | 62 | % | -160 | 160 | INT | 62
327 | P 2.4.4.4 | AI2 Custom Max | 100 | 62 | % | -160 | 160 | INT | 62
398 | P 2.4.4.5 | AI2 Signal Inv | 0 / No Inversion |  |  | 0 | 1 | BOOL
393 | P 2.4.4.6 | AI2 Scale Min | 0 | 60 |  | -32000 | 32000 | INT | 60
394 | P 2.4.4.7 | AI2 Scale Max | 0 | 60 |  | -32000 | 32000 | INT | 60
1511 | P 2.4.4.8 | AI2 Controll. ID | 0 | 60 |  | 0 | 10000 | UINT | 60
141 | P 2.4.5.1 | AI3 Signal Sel | AnIN:0.1 | 3 |  | AnIN:0.1 | AnIN:E.10 | INT | 3
142 | P 2.4.5.2 | AI3 Filter Time | 0 | 53 | s | 0 | 10 | INT | 53
144 | P 2.4.5.3 | AI3 Custom Min | 0 | 62 | % | -160 | 160 | INT | 62
145 | P 2.4.5.4 | AI3 Custom Max | 100 | 62 | % | -160 | 160 | INT | 62
151 | P 2.4.5.5 | AI3 Signal Inv | 0 / No Inversion |  |  | 0 | 1 | BOOL
1037 | P 2.4.5.6 | AI3 Scale Min | 0 | 60 |  | -32000 | 32000 | INT | 60
1038 | P 2.4.5.7 | AI3 Scale Max | 10000 | 60 |  | -32000 | 32000 | INT | 60
1509 | P 2.4.5.8 | AI3 Controll. ID | 0 | 60 |  | 0 | 10000 | UINT | 60
152 | P 2.4.6.1 | AI4 Signal Sel | AnIN:0.1 | 3 |  | AnIN:0.1 | AnIN:E.10 | INT | 3
153 | P 2.4.6.2 | AI4 Filter Time | 0 | 53 | s | 0 | 10 | INT | 53
155 | P 2.4.6.3 | AI4 Custom Min | 20 | 62 | % | -160 | 160 | INT | 62
156 | P 2.4.6.4 | AI4 Custom Max | 100 | 62 | % | -160 | 160 | INT | 62
162 | P 2.4.6.5 | AI4 Signal Inv | 0 / No Inversion |  |  | 0 | 1 | BOOL
1039 | P 2.4.6.6 | AI4 Scale Min | 0 | 60 |  | -32000 | 32000 | INT | 60
1040 | P 2.4.6.7 | AI4 Scale Max | 10000 | 60 |  | -32000 | 32000 | INT | 60
1510 | P 2.4.6.8 | AI4 Controll. ID | 0 | 60 |  | 0 | 10000 | UINT | 60
1218 | P 2.5.1.1 | MCB1 Close Cont | DigOUT:B.2 | 2 |  | DigOUT:0.1 | DigOUT:B.2 | INT | 2
1219 | P 2.5.1.2 | MCB1 Open Contr | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
432 | P 2.5.1.3 | Ready | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
433 | P 2.5.1.4 | Run | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
434 | P 2.5.1.5 | Common Fault | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
435 | P 2.5.1.6 | Fault, Inverted | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
442 | P 2.5.1.7 | At Ref. Speed | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
439 | P 2.5.1.8 | OverTemp Warn. | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
436 | P 2.5.1.9 | Warning | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1709 | P 2.5.1.10 | MCB2 Close Contr | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1605 | P 2.5.1.11 | NET CB Cont. | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1753 | P 2.5.1.12 | D7 Synchronized | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1568 | P 2.5.1.13 | DC Charge | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1684 | P 2.5.1.14 | Common Alarm | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1686 | P 2.5.1.15 | ReadyForStart | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1687 | P 2.5.1.16 | QuickStopActiv. | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
455 | P 2.5.1.17 | FB Dig Input 1 | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
891 | P 2.5.1.18 | FB Dig 1 Par ID | 0 | 40 | ID | 0 | 2000 | UINT | 40
456 | P 2.5.1.19 | FB Dig Input 2 | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
892 | P 2.5.1.20 | FB Dig 2 Par ID | 0 | 50 | ID | 0 | 2000 | UINT | 50
457 | P 2.5.1.21 | FB Dig Input 3 | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
893 | P 2.5.1.22 | FB Dig 3 Par ID | 0 | 50 | ID | 0 | 2000 | UINT | 50
169 | P 2.5.1.23 | FB Dig Input 4 | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
894 | P 2.5.1.24 | FB Dig 4 Par ID | 0 | 50 | ID | 0 | 2000 | UINT | 50
486 | P 2.5.2.1 | Dig.Out 1 Signal | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
312 | P 2.5.2.2 | DO1 Content | 0 / Not Used |  |  | 0 | 15 | INT
487 | P 2.5.2.3 | DO1 ON Delay | 0 | 62 | s | 0 | 320 | INT | 62
488 | P 2.5.2.4 | DO1 OFF Delay | 0 | 62 | s | 0 | 320 | INT | 62
1216 | P 2.5.2.5 | ID.Bit Free DO | 0 | 62 |  | 0 | 4000.15 | UDINT | 62
489 | P 2.5.3.1 | Dig.Out 2 Signal | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
490 | P 2.5.3.2 | DO2 Content | 0 / Not Used |  |  | 0 | 15 | INT
491 | P 2.5.3.3 | DO2 ON Delay | 0 | 62 | s | 0 | 320 | INT | 62
492 | P 2.5.3.4 | DO2 OFF Delay | 0 | 62 | s | 0 | 320 | INT | 62
1217 | P 2.5.3.5 | ID.Bit Free DO | 0 | 62 |  | 0 | 4000.15 | UDINT | 62
464 | P 2.5.4.1 | Iout 1 signal | AnOUT:0.1 | 4 |  | AnOUT:0.1 | AnOUT:E.10 | INT | 4
307 | P 2.5.4.2 | Iout Content | 0 / Not Used |  |  | 0 | 13 | INT
308 | P 2.5.4.3 | Iout Filter Time | 0.02 | 53 | s | 0 | 10 | INT | 53
309 | P 2.5.4.4 | Iout Invert | 0 / No Inversion |  |  | 0 | 1 | BOOL
310 | P 2.5.4.5 | Iout Minimum | 0 / 0 mA |  |  | 0 | 1 | BOOL
311 | P 2.5.4.6 | Iout Scale | 100 | 61 | % | 1 | 3200 | INT | 61
375 | P 2.5.4.7 | Iout Offset | 0 | 62 | % | -100 | 100 | INT | 62
471 | P 2.5.5.1 | Iout 2 Signal | AnOUT:0.1 | 4 |  | AnOUT:0.1 | AnOUT:E.10 | INT | 4
472 | P 2.5.5.2 | Iout 2 Content | 0 / Not Used |  |  | 0 | 13 | INT
473 | P 2.5.5.3 | Iout 2 Filter T | 0.02 | 53 | s | 0 | 10 | INT | 53
474 | P 2.5.5.4 | Iout 2 Invert | 0 / No Inversion |  |  | 0 | 1 | BOOL
475 | P 2.5.5.5 | Iout 2 Minimum | 0 / 0 mA |  |  | 0 | 1 | BOOL
476 | P 2.5.5.6 | Iout 2 Scale | 100 | 61 | % | 1 | 3200 | INT | 61
477 | P 2.5.5.7 | Iout 2 Offset | 0 | 62 | % | -100 | 100 | INT | 62
478 | P 2.5.6.1 | Iout 3 Signal | AnOUT:0.1 | 4 |  | AnOUT:0.1 | AnOUT:E.10 | INT | 4
479 | P 2.5.6.2 | Iout 3 Content | 0 / Not Used |  |  | 0 | 13 | INT
480 | P 2.5.6.3 | Iout 3 Filter T | 0.02 | 53 | s | 0 | 10 | INT | 53
481 | P 2.5.6.4 | Iout 3 Invert | 0 / No Inversion |  |  | 0 | 1 | BOOL
482 | P 2.5.6.5 | Iout 3 Minimum | 0 / 0 mA |  |  | 0 | 1 | BOOL
483 | P 2.5.6.6 | Iout 3 Scale | 100 | 61 | % | 1 | 3200 | INT | 61
484 | P 2.5.6.7 | Iout 3 Offset | 0 | 62 | % | -100 | 100 | INT | 62
1806 | P 2.5.7.1 | Output Inversion | 0 | 60 |  | 0 | 65535 | UINT | 60
1454 | P 2.5.7.2 | DC Superv. Limit | 436 | 50 | V | 0 | 1100 | UINT | 50
1607 | P 2.5.7.3 | MCB Close Mode | 0 / DC Voltage |  |  | 0 | 3 | INT
1685 | P 2.5.7.4 | MCB At Stop Comm | 0 / No Action |  |  | 0 | 1 | BOOL
1513 | P 2.5.7.5 | MCB Close Delay | 0 | 62 | s | 0 | 3 | INT | 62
4531 | P 2.5.7.6 | GridCodeBreaker | 0 / MCB 1 |  |  | 0 | 1 | INT
107 | P 2.6.1.1 | Current Limit | 460 | 60 | A | 0 | 693 | UINT | CurrentFormat
1620 | P 2.6.1.2 | ShortCircuitLevl | 800 | 61 | % | 0 | 800 | INT | 61
1515 | P 2.6.1.3 | ShortCircuitTime | 0 | 90 | ms | 0 | 5000 | DINT | 90
1517 | P 2.6.1.4 | BridgeCurr.Limit | 0 / Enabled |  |  | 0 | 1 | BOOL
1518 | P 2.6.1.5 | BiPhsFaultVLevel | 80 | 62 | % | 0 | 150 | UINT | 62
1290 | P 2.6.1.6 | OutputActCurrLim | 150 | 61 | % | -320 | 320 | INT | 61
1289 | P 2.6.1.7 | InputActCurrLim | 150 | 61 | % | -320 | 320 | INT | 61
1094 | P 2.6.1.8 | OverCurrTripLim | 0 | 61 | % | 0 | 1000 | INT | 61
1288 | P 2.6.2.1 | OutputPowerLimit | 150 | 61 | % | 0 | 300 | INT | 61
1287 | P 2.6.2.2 | InputPowerLimit | 150 | 61 | % | 0 | 300 | INT | 61
1502 | P 2.6.2.3 | Limit.Inc.Rate | 100 | 60 | %/s | 0 | 10000 | INT | 60
1703 | P 2.6.2.4 | HighFreqPowerLim | 0 | 62 | Hz | 0 | 100 | INT | 62
1812 | P 2.6.2.5 | StopPowrRampRate | -0.01 | 62 | %/s | -1 | 100 | INT | 62
1717 | P 2.6.3.1 | LineLowTripLim | 40 | 62 | Hz | 0 | 120 | INT | FreqFormat
1716 | P 2.6.3.2 | LineHighTripLim | 70 | 62 | Hz | 0 | 120 | INT | FreqFormat
1621 | P 2.6.4.1 | CurrentLimitMin | -150 | 61 | % | -300 | 0 | INT | 61
1622 | P 2.6.4.2 | CurrentLimitMax | 150 | 61 | % | 0 | 300 | INT | 61
1502 | P 2.6.4.3 | Limit.Inc.Rate | 100 | 60 | %/s | 0 | 10000 | INT | 60
1623 | P 2.6.4.4 | Current Limit Kp | 70 | 60 |  | 0 | 1000 | INT | 60
1625 | P 2.6.4.5 | Current Limit Ti | 32 | 60 | ms | 0 | 1000 | INT | 60
1890 | P 2.6.4.6 | CurrLimMaxMinimu | 1 | 61 | % | 0 | 10 | INT | 61
1539 | P 2.6.4.7 | CurLimToZeroMode | 0 / No Action |  |  | 0 | 1 | INT
1524 | P 2.6.5.1 | UnderVoltageLim | 65 | 62 | % | 0 | 130 | INT | 62
1523 | P 2.6.5.2 | OverVoltageLim | 125 | 62 | % | 50 | 130 | INT | 62
504 | P 2.6.5.3 | Brake Chopper | 0 / Not Used |  |  | 0 | 3 | INT
1267 | P 2.6.5.4 | BrakeChopperLev | 797 | 60 | Vdc | 605 | 797 | UINT | 60
1525 | P 2.6.5.5 | DCLimControl Kp | 100 | 60 |  | 0 | 32000 | INT | 60
1526 | P 2.6.5.6 | DCLimControl Ti | 50 | 60 | ms | 0 | 32000 | INT | 60
1251 | P 2.6.5.7 | HighMCBCloseLim | 0 | 60 | Vdc | 0 | 1300 | UINT | 60
1813 | P 2.6.5.8 | LK Low DC | 0 | 60 |  | 0 | 65535 | UINT | 60
601 | P 2.7.1 | Switching Freq | 3.6 | 61 | kHz | 3.6 | 6 | UINT | 61
1463 | P 2.7.2 | AFEOptions 1 | 544 | 60 |  | 0 | 65535 | WORD | 60
1464 | P 2.7.3 | AFEOptions 2 | 0 | 60 |  | 0 | 65535 | WORD | 60
1466 | P 2.7.4 | AFEOptions 3 | 0 | 60 |  | 0 | 65535 | WORD | 60
1467 | P 2.7.5 | AFEOptions 4 | 0 | 60 |  | 0 | 65535 | WORD | 60
1500 | P 2.7.6 | Start Delay | 1 | 62 | s | 0 | 320 | INT | 62
1516 | P 2.7.7 | ModulatorType | 1 / Software 1 |  |  | 0 | 4 | USINT
1707 | P 2.7.8 | Control Options | 0 | 60 |  | 0 | 65535 | UINT | 60
1798 | P 2.7.9 | Control Options2 | 0 | 60 |  | 0 | 65535 | UINT | 60
1855 | P 2.7.10 | Operation Time | 0 | 100 |  | 0 | 4294967295 | UDINT | 100
1797 | P 2.7.11.1 | DynamicSupportKp | 0 | 60 |  | 0 | 32000 | INT | 60
1457 | P 2.7.11.2 | Sync Kp | 2000 | 60 |  | 0 | 32000 | INT | 60
1458 | P 2.7.11.3 | Sync Ti | 50 | 60 |  | 0 | 1000 | INT | 60
1455 | P 2.7.11.4 | ActiveCurrentKp | 400 | 40 |  | 0 | 4000 | INT | 40
1456 | P 2.7.11.5 | ActiveCurrentTi | 15 | 40 |  | 0 | 1000 | INT | 40
1698 | P 2.7.11.6 | Synch Kp Start | 4000 | 60 |  | 0 | 32000 | INT | 60
1451 | P 2.7.11.7 | Voltage Ctrl Kp | 200 | 60 |  | 0 | 32000 | INT | 60
1452 | P 2.7.11.8 | Voltage Ctrl Ti | 50 | 50 | ms | 0 | 1000 | INT | 50
1682 | P 2.7.11.9 | Mod#2 Opt. DPWM | 1 / Enabled |  |  | 0 | 1 | BOOL
1560 | P 2.7.11.10 | AdvancedOptions1 | 0 | 60 |  | 0 | 65535 | WORD | 60
1561 | P 2.7.11.11 | AdvancedOptions2 | 0 | 60 |  | 0 | 65535 | WORD | 60
1563 | P 2.7.11.12 | AdvancedOptions4 | 0 | 60 |  | 0 | 65535 | WORD | 60
1564 | P 2.7.11.13 | AdvancedOptions5 | 0 | 60 |  | 0 | 65535 | WORD | 60
1565 | P 2.7.11.14 | AdvancedOptions6 | 0 | 60 |  | 0 | 65535 | WORD | 60
668 | P 2.7.12.1 | IU Offset | 10000 | 60 |  | -32000 | 32000 | INT | 60
669 | P 2.7.12.2 | IV Offset | 0 | 60 |  | -32000 | 32000 | INT | 60
670 | P 2.7.12.3 | IW Offset | 0 | 60 |  | -32000 | 32000 | INT | 60
549 | P 2.7.12.4 | DCLinkMeasCalib | 0 | 62 | % | -2 | 2 | INT | 62
1900 | P 2.7.13.1 | DCRip.Comp Kp | 0 | 60 |  | 0 | 1000 | INT | 60
1901 | P 2.7.13.2 | DCRip.CompPhase | 0 | 60 |  | -360 | 360 | INT | 60
1902 | P 2.7.13.3 | DCRip.Comp Freq | 300 | 60 | Hz | 0 | 1000 | INT | 60
1938 | P 2.7.13.4 | HarmCompDroop | 100 | 60 |  | -32000 | 32000 | INT | 60
1939 | P 2.7.13.5 | HarmCompDroopHi | 100 | 60 |  | -32000 | 32000 | INT | 60
1324 | P 2.8.1 | MF Mode | 0 / No Communica |  |  | 0 | 6 | INT
1081 | P 2.8.2 | FollowerDCRef | 0 / Master Ref. |  |  | 0 | 1 | INT
1994 | P 2.8.3 | MF License | 0 | 60 |  | 0 | 65535 | UINT | 60
732 | P 2.9.1.1 | ThermistorF.Resp | 2 / Fault |  |  | 0 | 2 | INT
1757 | P 2.9.1.2 | OverTemp Resp | 2 / Fault |  |  | 2 | 5 | INT
1755 | P 2.9.1.3 | Overvoltage Resp | 2 / Fault |  |  | 2 | 5 | INT
751 | P 2.9.1.4 | CoolingFlt.Delay | 2 | 32 | s | 0 | 7 | INT | 32
1505 | P 2.9.1.5 | LCL Over Tempera | 2 / Fault |  |  | 0 | 2 | INT
1522 | P 2.9.1.6 | Max Charge Time | 10 | 52 | s | 0 | 30 | INT | 52
1699 | P 2.9.1.7 | MCB At Fault | 0 / No Action |  |  | 0 | 1 | BOOL
1758 | P 2.9.1.8 | QuickStopRespon. | 1 / Warning |  |  | 1 | 2 | INT
1759 | P 2.9.1.9 | ReacErrorTripLim | 7.5 | 61 | % | -3200 | 3200 | INT | 61
1521 | P 2.9.1.10 | MCB Fault Delay | 3.5 | 42 | s | 0 | 10 | INT | 42
702 | P 2.9.1.11 | Line Ph. Supervi | 0 / No Action |  |  | 0 | 2 | INT
700 | P 2.9.1.12 | 4mA Fault Resp | 0 / No Action |  |  | 0 | 2 | INT
1981 | P 2.9.1.13 | Reactive Respon. | 1 / Warning |  |  | 0 | 2 | INT
739 | P 2.9.2.1 | Board1 Channels | 0 | 10 |  | 0 | 5 | INT | 10
740 | P 2.9.2.2 | Board1 Response | 2 / Fault |  |  | 0 | 3 | INT
741 | P 2.9.2.3 | Board1 Warn.Lim | 120 | 51 | °C | -30 | 200 | INT | 51
742 | P 2.9.2.4 | Board1 FaultLim. | 130 | 51 | °C | -30 | 200 | INT | 51
743 | P 2.9.2.5 | Board2 Channels | 0 | 10 |  | 0 | 5 | INT | 10
766 | P 2.9.2.6 | Board2 Response | 0 / No Action |  |  | 0 | 3 | INT
745 | P 2.9.2.7 | Board2 Warn.Lim | 120 | 61 | °C | -30 | 200 | INT | 61
746 | P 2.9.2.8 | Board2 Fault.Lim | 130 | 61 | °C | -30 | 200 | INT | 61
764 | P 2.9.2.9.1 | Channel 1B Warn | 0 | 61 | °C | -30 | 200 | INT | 61
765 | P 2.9.2.9.2 | Channel 1B Fault | 0 | 61 | °C | -30 | 200 | INT | 61
768 | P 2.9.2.9.3 | Channel 1C Warn | 0 | 61 | °C | -30 | 200 | INT | 61
769 | P 2.9.2.9.4 | Channel 1C Fault | 0 | 61 | °C | -30 | 200 | INT | 61
770 | P 2.9.2.9.5 | Channel 2B Warn | 0 | 61 | °C | -30 | 200 | INT | 61
771 | P 2.9.2.9.6 | Channel 2B Fault | 0 | 61 | °C | -30 | 200 | INT | 61
772 | P 2.9.2.9.7 | Channel 2C Warn | 0 | 61 | °C | -30 | 200 | INT | 61
773 | P 2.9.2.9.8 | Channel 2C Fault | 0 | 61 | °C | -30 | 200 | INT | 61
1756 | P 2.9.3.1 | EarthFlt Resp | 2 / Fault |  |  | 2 | 5 | INT
1333 | P 2.9.3.2 | EarthFaultLevel | 50 | 51 | % | 0 | 100 | UINT | 51
733 | P 2.9.4.1 | FBFaultSlotDResp | 2 / Fault |  |  | 0 | 6 | INT
761 | P 2.9.4.2 | FBFaultSlotEResp | 2 / Fault |  |  | 0 | 6 | INT
1354 | P 2.9.4.3 | FB WD Time | 0 | 62 | s | 0 | 30 | INT | 62
701 | P 2.9.5.1 | External Fault 1 | 2 / Fault |  |  | 0 | 3 | INT
1504 | P 2.9.5.2 | External Fault 2 | 1 / Warning |  |  | 0 | 3 | INT
1506 | P 2.9.5.3 | Ext Fault Delay | 0.1 | 62 | s | 0 | 320 | INT | 62
1626 | P 2.9.6.1 | Volt. D7 Respons | 1 / Warning |  |  | 0 | 2 | INT
1893 | P 2.9.6.2 | VoltLowWarnLim | 90 | 62 | % | 0 | 320 | INT | 62
1899 | P 2.9.6.3 | VoltLowTripLim | 80 | 62 | % | 0 | 115 | INT | 62
1895 | P 2.9.6.4 | VoltHighWarnLim | 110 | 62 | % | 0 | 320 | INT | 62
1799 | P 2.9.6.5 | VoltHighTripLim | 115 | 62 | % | 80 | 320 | INT | 62
1898 | P 2.9.6.6 | VoltageTripDelay | 0.5 | 62 | s | 0 | 320 | INT | 62
1627 | P 2.9.7.1 | Freq.Supply Resp | 2 / Fault |  |  | 0 | 2 | INT
1628 | P 2.9.7.2 | Freq. D7 Respons | 1 / Warning |  |  | 0 | 2 | INT
1780 | P 2.9.7.3 | FreqLowWarnLim | 95 | 62 | % | 0 | 320 | INT | 62
1788 | P 2.9.7.4 | FreqLowTripLim | 94 | 62 | % | 0 | 320 | INT | 62
1786 | P 2.9.7.5 | FreqHighWarnLim | 106 | 62 | % | 0 | 320 | INT | 62
1787 | P 2.9.7.6 | FreqHighTripLim | 110 | 62 | % | 0 | 320 | INT | 62
1785 | P 2.9.7.7 | Freq. Trip Delay | 0.5 | 62 | s | 0 | 320 | INT | 62
1629 | P 2.9.8.1 | Volt.Supply Resp | 2 / Fault |  |  | 0 | 2 | INT
1891 | P 2.9.8.2 | VoltOutTripLLim | 75 | 62 | % | 0 | 320 | UINT | 62
1880 | P 2.9.8.3 | VoltOutWarnLLim | 90 | 62 | % | 0 | 320 | UINT | PowerRefRampFormat
1881 | P 2.9.8.4 | VoltOutWarnHLim | 120 | 62 | % | 0 | 320 | UINT | 62
1892 | P 2.9.8.5 | VoltOutTripHLim | 130 | 62 | % | 0 | 320 | UINT | 62
1838 | P 2.9.9.1 | OverLoadResponse | 0 / No Action |  |  | 0 | 2 | USINT
1837 | P 2.9.9.2 | OverLoadSignal | 0 / Not Used |  |  | 0 | 3 | INT
1839 | P 2.9.9.3 | OverLoadMaxIn | 150 | 61 | % | 0 | 300 | INT | 61
1840 | P 2.9.9.4 | OverLoadMaxStep | 200 | 60 |  | 0 | 10000 | INT | 60
1672 | P 2.9.10.1 | THD Respons. | 0 / No Action |  |  | 0 | 2 | INT
1673 | P 2.9.10.2 | THD Warn. Limit | 6 | 62 | % | 0 | 50 | INT | 62
1674 | P 2.9.10.3 | THD Fault Limit | 10 | 62 | % | 0 | 50 | INT | 62
1675 | P 2.9.10.4 | HF rms Respon. | 0 / No Action |  |  | 0 | 2 | INT
1676 | P 2.9.10.5 | HF rms WarnLim | 20 | 61 | V | 0 | 400 | INT | 61
1677 | P 2.9.10.6 | HF rms FaultLim | 60 | 61 | V | 0 | 400 | INT | 61
1569 | P 2.9.11 | Fault Simulation | 0 | 60 |  | 0 | 65535 | UINT | 60
1857 | P 2.9.12 | ResetDatalogger | 0 / Auto |  |  | 0 | 4 | INT
1086 | P 2.9.13 | Disable StopLock | 0 / No |  |  | 0 | 1 | BOOL
1853 | P 2.10.1 | FBActualValueSel | 1108 | 60 | ID | 0 | 10000 | UINT | 60
852 | P 2.10.2 | FB Data Out1 Sel | 1104 | 50 |  | 0 | 10000 | UINT | 50
853 | P 2.10.3 | FB Data Out2 Sel | 1508 | 50 |  | 0 | 10000 | UINT | 50
854 | P 2.10.4 | FB Data Out3 Sel | 1172 | 50 |  | 0 | 10000 | UINT | 50
855 | P 2.10.5 | FB Data Out4 Sel | 1173 | 50 |  | 0 | 10000 | UINT | 50
856 | P 2.10.6 | FB Data Out5 Sel | 56 | 50 |  | 0 | 10000 | UINT | 50
857 | P 2.10.7 | FB Data Out6 Sel | 1174 | 50 |  | 0 | 10000 | UINT | 50
858 | P 2.10.8 | FB Data Out7 Sel | 1125 | 50 |  | 0 | 10000 | UINT | 50
859 | P 2.10.9 | FB Data Out8 Sel | 1157 | 50 |  | 0 | 10000 | UINT | 50
876 | P 2.10.18 | FB Data In 1 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
877 | P 2.10.19 | FB Data In 2 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
878 | P 2.10.20 | FB Data In 3 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
879 | P 2.10.21 | FB Data In 4 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
880 | P 2.10.22 | FB Data In 5 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
881 | P 2.10.23 | FB Data In 6 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
882 | P 2.10.24 | FB Data In 7 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
883 | P 2.10.25 | FB Data In 8 Sel | 0 | 50 |  | 0 | 10000 | UINT | 50
897 | P 2.10.34 | GSW Data | 68 | 60 |  | 0 | 10000 | UINT | 60
896 | P 2.10.35 | State Machine | 2 / Vacon AFE 1 |  |  | 0 | 4 | INT
1440 | P 2.10.36 | ControlSlotSel. | 0 / No Sel |  |  | 0 | 0 | USINT
1907 | P 2.10.37 | SW B11 ID.Bit | 0 | 62 |  | 0 | 2000 | UDINT | 62
1908 | P 2.10.38 | SW B12 ID.Bit | 0 | 62 |  | 0 | 2000 | UDINT | 62
1909 | P 2.10.39 | SW B13 ID.Bit | 0 | 62 |  | 0 | 2000 | UDINT | 62
1910 | P 2.10.40 | SW B14 ID.Bit | 0 | 62 |  | 0 | 2000 | UDINT | 62
1934 | P 2.10.41 | uCW B12 | 0 | 60 | ID | 0 | 10000 | UINT | 60
1935 | P 2.10.42 | uCW B13 | 0 | 60 | ID | 0 | 10000 | UINT | 60
1936 | P 2.10.43 | uCW B14 | 0 | 60 | ID | 0 | 10000 | UINT | 60
1937 | P 2.10.44 | uCW B15 | 0 | 60 | ID | 0 | 10000 | UINT | 60
1531 | P 2.11.1 | Control Mode | 0 / AFE |  |  | 0 | 6 | INT
1534 | P 2.11.2 | FrequencyDroop | 1 | 63 | Hz | -32 | 32 | INT | 63
1535 | P 2.11.3 | Voltage Droop | 5 | 62 | % | 0 | 320 | INT | 62
1503 | P 2.11.4 | StartPowerMode | 2 / Drooping |  |  | 0 | 3 | INT
1541 | P 2.11.5 | VoltageRiseTime | 100 | 60 | ms | 50 | 10000 | INT | 60
1722 | P 2.11.6 | Gener.Mech. TC | 0 | 60 | ms | 0 | 32000 | INT | 60
1723 | P 2.11.7 | Gener.Speed Kp | 40 | 61 |  | 0 | 3200 | INT | 61
1724 | P 2.11.8 | Gener.Speed Ti | 500 | 60 | ms | 0 | 32000 | INT | 60
1616 | P 2.11.9.1 | AFE Mode 1 | 0 / AFE |  |  | 0 | 6 | USINT
1617 | P 2.11.9.2 | AFE Mode 2 | 1 / Island |  |  | 0 | 6 | USINT
1713 | P 2.11.9.3 | AFE Mode 3 | 2 / uGrid |  |  | 0 | 6 | USINT
1601 | P 2.12.1 | Synch. Offset | 0 | 60 |  | -3172 | 3171 | INT | 60
1611 | P 2.12.2 | Synch Reference | 0 | 60 |  | -3170 | 3170 | INT | 60
1612 | P 2.12.3 | Synch Kp | 500 | 60 |  | 0 | 32000 | INT | 60
1613 | P 2.12.4 | Synch Ti | 0 | 60 |  | 0 | 32000 | INT | 60
1614 | P 2.12.5 | Synch.Hysteresis | 50 | 60 |  | -3170 | 3170 | INT | 60
1624 | P 2.12.6 | Contactor Delay | 0 | 60 | ms | 0 | 1000 | DINT | 60
1618 | P 2.12.7 | Synch Stop Mode | 0 / Stay Run |  |  | 0 | 1 | INT
1580 | P 2.14.1.1 | ContrInSignal ID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1581 | P 2.14.1.2 | Contrl Off Limit | 0 | 60 |  | -32000 | 32000 | INT | 60
1582 | P 2.14.1.3 | Contrl On Limit | 0 | 60 |  | -32000 | 32000 | INT | 60
1583 | P 2.14.1.4 | Contrl Off Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1584 | P 2.14.1.5 | Contrl On Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1585 | P 2.14.1.6 | ControlOutSignID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1590 | P 2.14.1.7 | Control Mode | 0 / SR ABS |  |  | 0 | 5 | INT
1721 | P 2.14.1.8 | Control Filt TC | 0 | 63 | s | 0 | 32 | INT | 63
1570 | P 2.14.2.1 | ID Control DIN | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1571 | P 2.14.2.2 | Controlled ID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1572 | P 2.14.2.3 | FALSE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1573 | P 2.14.2.4 | TRUE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1574 | P 2.14.3.1 | ID Control DIN | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1575 | P 2.14.3.2 | Controlled ID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1576 | P 2.14.3.3 | FALSE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1577 | P 2.14.3.4 | TRUE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1578 | P 2.14.4.1 | ID Control DIN | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1579 | P 2.14.4.2 | Controlled ID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1587 | P 2.14.4.3 | FALSE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1588 | P 2.14.4.4 | TRUE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1930 | P 2.14.5.1 | ID Control DIN | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
1931 | P 2.14.5.2 | Controlled ID | 0 | 60 | ID | 0 | 10000 | UINT | 60
1932 | P 2.14.5.3 | FALSE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1933 | P 2.14.5.4 | TRUE Value | 0 | 60 |  | -32000 | 32000 | INT | 60
1385 | P 2.14.6.1 | ID.Bit Free DO1 | 0 | 62 |  | 0 | 4000.15 | UDINT | 62
1326 | P 2.14.6.2 | Free DO1 Sel. | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
1386 | P 2.14.7.1 | ID.Bit Free DO2 | 0 | 62 |  | 0 | 4000.15 | UDINT | 62
1325 | P 2.14.7.2 | Free DO2 Sel. | DigOUT:0.1 | 2 |  | DigOUT:0.1 | DigOUT:E.10 | INT | 2
717 | P 2.15.1 | Wait Time | 0.5 | 62 | s | 0 | 60 | UINT | 62
718 | P 2.15.2 | Trial Time | 30 | 62 | s | 0 | 120 | UINT | 62
721 | P 2.15.3 | Overvolt. Tries | 0 | 60 |  | 0 | 3 | USINT | 60
722 | P 2.15.4 | Overcurr. Tries | 0 | 60 |  | 0 | 3 | USINT | 60
725 | P 2.15.5 | Ext.Fault Tries | 0 | 60 |  | 0 | 10 | USINT | 60
1807 | P 2.16.1 | PID Activation | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
118 | P 2.16.2 | PID-Contr Gain | 200 | 61 | % | -3200 | 3200 | INT | 61
119 | P 2.16.3 | PID-Contr I Time | 0.05 | 62 | s | -0.1 | 320 | INT | 62
360 | P 2.16.4 | PI Max Adjust +- | 5 | 62 |  | -320 | 320 | INT | 62
1630 | P 2.16.5.1 | PI Freq Low Lim | 95 | 62 | % | 0 | 320 | INT | 62
1631 | P 2.16.5.2 | PI Freq High Lim | 102 | 62 | % | 0 | 320 | INT | 62
1632 | P 2.16.5.3 | PI Volt Low Lim | 90 | 62 | % | 0 | 320 | INT | 62
1633 | P 2.16.5.4 | PI Volt High Lim | 110 | 62 | % | 0 | 320 | INT | 62
3201 | P 2.17.1 | GridCode License | 0 | 60 |  | 0 | 65535 | UINT | 60
3401 | P 2.17.2 | Set Grid Code | 0 / No Action |  |  | 0 | 40 | INT
3254 | P 2.17.3 | EnableGridCode | 0 / Disabled |  |  | 0 | 4 | INT
3250 | P 2.17.4.1 | Anti-Islanding | 0 / Disabled |  |  | 0 | 1 | INT
3322 | P 2.17.4.2 | LF MaxChangeRate | 2.5 | 62 | Hz/s | 0 | 20 | INT | 62
3404 | P 2.17.4.3 | High Volt AI | 0 | 62 | % | 0 | 320 | INT | 62
3405 | P 2.17.4.4 | Low Volt AI | 0 | 62 | % | 0 | 320 | INT | 62
3406 | P 2.17.4.5 | High Freq AI | 110 | 62 | % | 0 | 320 | INT | 62
3407 | P 2.17.4.6 | Low Freq. AI | 80 | 62 | % | 0 | 320 | INT | 62
3408 | P 2.17.4.7 | AI Trip Delay | 50 | 100 | ms | 0 | 10000 | DINT | 100
3426 | P 2.17.4.8 | AntiIslanding Kp | 0 | 60 | % | 0 | 5000 | INT | 60
3251 | P 2.17.5.1 | FRT Function | 0 / Disab;Both |  |  | 0 | 4 | INT
3252 | P 2.17.5.2 | ReactivInjection | 0 / Tri:N, Bi:N |  |  | 0 | 2 | INT
3323 | P 2.17.5.3 | Symmet.Reactive | 1 / Yes |  |  | 0 | 1 | BOOL
3284 | P 2.17.5.4.1 | Voltage X6 | 0 | 102 | % | 0 | 110 | DINT | 102
3285 | P 2.17.5.4.2 | Time Y6 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3282 | P 2.17.5.4.3 | Voltage X5 | 0 | 102 | % | 0 | 110 | DINT | 102
3283 | P 2.17.5.4.4 | Time Y5 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3280 | P 2.17.5.4.5 | Voltage X4 | 0 | 102 | % | 0 | 110 | DINT | 102
3281 | P 2.17.5.4.6 | Time Y4 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3278 | P 2.17.5.4.7 | Voltage X3 | 0 | 102 | % | 0 | 110 | DINT | 102
3279 | P 2.17.5.4.8 | Time Y3 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3276 | P 2.17.5.4.9 | Voltage X2 | 0 | 102 | % | 0 | 110 | DINT | 102
3277 | P 2.17.5.4.10 | Time Y2 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3274 | P 2.17.5.4.11 | Voltage X1 | 0 | 102 | % | 0 | 110 | DINT | 102
3275 | P 2.17.5.4.12 | Time Y1 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3272 | P 2.17.5.4.13 | Voltage X0 | 0 | 102 | % | 0 | 110 | DINT | 102
3273 | P 2.17.5.4.14 | Time Y0 | 0 | 100 | ms | 0 | 20000 | DINT | 100
3253 | P 2.17.6.1 | ReConnectTime | 2 | 103 | s | 1.1 | 1000 | DINT | 103
3255 | P 2.17.6.2 | ReConnTimeStop | 2 | 103 | s | 1.1 | 1000 | DINT | 103
3297 | P 2.17.6.3 | ReConRampUpRate | 20 | 62 | %/s | -1 | 320 | INT | 62
3421 | P 2.17.6.4 | RampReleaseDelay | 600 | 60 | ms | 0 | 32000 | DINT | 60
3287 | P 2.17.6.5 | LF OK High | 0 | 62 | % | 0 | 200 | INT | 62
3286 | P 2.17.6.6 | LF OK Low | 0 | 62 | % | 0 | 110 | INT | 62
3289 | P 2.17.6.7 | LV OK High | 0 | 62 | % | 0 | 200 | INT | 62
3288 | P 2.17.6.8 | LV OK Low | 0 | 62 | % | 0 | 110 | INT | 62
3290 | P 2.17.6.9 | Line OK Delay | 0 | 100 | ms | 0 | 60000 | DINT | 100
3364 | P 2.17.7.1 | VoltageMonitor | 1 / PhaseMinMax |  |  | 0 | 3 | INT
3256 | P 2.17.7.2 | LV High 1 | 115 | 62 | % | 0 | 200 | INT | 62
3257 | P 2.17.7.3 | LV High 1 Delay | 50 | 100 | ms | 0 | 120000 | DINT | 100
3412 | P 2.17.7.4 | LV High 1 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3258 | P 2.17.7.5 | LV High 2 | 0 | 62 | % | 0 | 200 | INT | 62
3259 | P 2.17.7.6 | LV High 2 Delay | 0 | 100 | ms | 0 | 120000 | DINT | 100
3413 | P 2.17.7.7 | LV High 2 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3361 | P 2.17.7.8 | LV High 3 | 0 | 62 | % | 0 | 200 | INT | 62
3362 | P 2.17.7.9 | LV High 3 Delay | 0 | 100 | ms | 0 | 120000 | DINT | 100
3363 | P 2.17.7.10 | LV High 3 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3260 | P 2.17.7.11 | LV Low 1 | 0 | 62 | % | 0 | 200 | INT | 62
3261 | P 2.17.7.12 | LV Low 1 Delay | 0 | 100 | ms | 0 | 120000 | DINT | 100
3414 | P 2.17.7.13 | LV Low 1 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3262 | P 2.17.7.14 | LV Low 2 | 80 | 62 | % | 0 | 200 | INT | 62
3263 | P 2.17.7.15 | LV Low 2 Delay | 50 | 100 | ms | 0 | 120000 | DINT | 100
3415 | P 2.17.7.16 | LV Low 2 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3365 | P 2.17.7.17 | LV Low 3 | 0 | 62 | % | 0 | 200 | INT | 62
3366 | P 2.17.7.18 | LV Low 3 Delay | 0 | 100 | ms | 0 | 120000 | DINT | 100
3367 | P 2.17.7.19 | LV Low 3 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3416 | P 2.17.7.20 | LV Low 4 | 0 | 62 | % | 0 | 200 | INT | 62
3417 | P 2.17.7.21 | LV Low 4 Delay | 160 | 100 | ms | 0 | 120000 | DINT | 100
3418 | P 2.17.7.22 | LV Low 4 PLim | -1 | 61 | % | -1 | 300 | INT | 61
3353 | P 2.17.7.23 | 10MinAveHighVolt | 0 | 62 | % | 0 | 200 | INT | 62
3376 | P 2.17.7.24 | 10minAvTripDelay | 50 | 100 | ms | 0 | 60000 | DINT | 100
3410 | P 2.17.7.25 | VoltResponceTime | 0 | 60 | ms | 0 | 500 | DINT | 60
3419 | P 2.17.7.26 | PLim Down Rate | 100 | 60 | %/s | -100 | 32000 | INT | 60
3423 | P 2.17.8.1 | FrequencyMonitor | 0 / Normal |  |  | 0 | 1 | INT
3264 | P 2.17.8.2 | LF High 1 | 103 | 62 | % | 0 | 200 | INT | 62
3265 | P 2.17.8.3 | LF High 1 Delay | 50 | 100 | ms | 0 | 1200000 | DINT | 100
3266 | P 2.17.8.4 | LF High 2 | 0 | 62 | % | 0 | 200 | INT | 62
3267 | P 2.17.8.5 | LF High 2 Delay | 0 | 100 | ms | 0 | 1200000 | DINT | 100
3368 | P 2.17.8.6 | LF High 3 | 0 | 62 | % | 0 | 200 | INT | 62
3369 | P 2.17.8.7 | LF High 3 Delay | 0 | 100 | ms | 0 | 1200000 | DINT | 100
3268 | P 2.17.8.8 | LF Low 1 | 0 | 62 | % | 0 | 200 | INT | 62
3269 | P 2.17.8.9 | LF Low 1 Delay | 0 | 100 | ms | 0 | 1200000 | DINT | 100
3270 | P 2.17.8.10 | LF Low 2 | 95 | 62 | % | 0 | 200 | INT | 62
3271 | P 2.17.8.11 | LF Low 2 Delay | 50 | 100 | ms | 0 | 1200000 | DINT | 100
3370 | P 2.17.8.12 | LF Low 3 | 0 | 62 | % | 0 | 200 | INT | 62
3371 | P 2.17.8.13 | LF Low 3 Delay | 0 | 1000 | ms | 0 | 1200000 | DINT | 1000
3322 | P 2.17.8.14 | LF MaxChangeRate | 2.5 | 62 | Hz/s | 0 | 20 | INT | 62
3399 | P 2.17.8.15 | FreqResponceTime | 0 | 60 | ms | 0 | 500 | DINT | 60
3411 | P 2.17.8.16 | TOffCycles | 2 | 60 | x | 0 | 10 | INT | 60
3314 | P 2.17.9.1 | UV Reactive Mode | 0 / Linear |  |  | 0 | 2 | INT
3377 | P 2.17.9.2 | OV Reactive Mode | 0 / Linear |  |  | 0 | 1 | INT
3291 | P 2.17.9.3.1 | UV High Corner | 0 | 62 | % | 0 | 200 | INT | 62
3292 | P 2.17.9.3.2 | UV Low Corner | 0 | 62 | % | 0 | 200 | INT | 62
3293 | P 2.17.9.3.3 | UV Reac.MaxRef | 0 | 61 | % | 0 | 250 | INT | 61
3294 | P 2.17.9.3.4 | UV Bi Reac. Ref | 0 | 61 | % | 0 | 250 | INT | 61
3300 | P 2.17.9.4.1 | OV Low Corner | 0 | 62 | % | 0 | 150 | INT | 62
3301 | P 2.17.9.4.2 | OV Max Reactiv | 0 | 61 | % | 0 | 250 | INT | 61
3302 | P 2.17.9.4.3 | OV React Slope | 0 | 62 | %/% | 0 | 320 | INT | 62
3303 | P 2.17.9.4.4 | OV React PLogIn | 0 | 61 | % | 0 | 150 | INT | 61
3329 | P 2.17.9.4.5 | OV React PLogOut | 0 | 61 | % | 0 | 150 | INT | 61
3315 | P 2.17.9.5.1 | UV PowerLockIn | 0 | 61 | % | -1 | 200 | INT | 61
3316 | P 2.17.9.5.2 | UV PowerLockOut | 0 | 61 | % | -1 | 200 | INT | 61
3372 | P 2.17.9.5.3 | UV PowrLogInMode | 0 / VoltLevlTrig |  |  | 0 | 1 | INT
3291 | P 2.17.9.5.4 | UV High Corner | 0 | 62 | % | 0 | 200 | INT | 62
3292 | P 2.17.9.5.5 | UV Low Corner | 0 | 62 | % | 0 | 200 | INT | 62
3317 | P 2.17.9.5.6 | UV LockOutVoltag | 0 | 62 | % | 0 | 200 | INT | 62
3318 | P 2.17.9.5.7 | UV ReacHalfRef | 0 | 61 | % | 0 | 250 | INT | 61
3293 | P 2.17.9.5.8 | UV Reac.MaxRef | 0 | 61 | % | 0 | 250 | INT | 61
3294 | P 2.17.9.5.9 | UV Bi ReacMaxRef | 0 | 61 | % | 0 | 250 | INT | 61
3444 | P 2.17.9.5.10 | UV Reac.Start V | 0 | 62 | % | 0 | 320 | INT | 62
3378 | P 2.17.9.6.1 | OV PowerLockIn | 0 | 61 | % | 0 | 200 | INT | 61
3379 | P 2.17.9.6.2 | OV PowerLockOut | 0 | 61 | % | 0 | 200 | INT | 61
3380 | P 2.17.9.6.3 | OV PowrLogInMode | 0 / VoltLevlTrig |  |  | 0 | 1 | INT
3300 | P 2.17.9.6.4 | OV Low Corner | 0 | 62 | % | 0 | 150 | INT | 62
3320 | P 2.17.9.6.5 | OV High Corner | 0 | 62 | % | 0 | 300 | INT | 62
3319 | P 2.17.9.6.6 | OV LockOutVoltag | 0 | 62 | % | 0 | 200 | INT | 62
3321 | P 2.17.9.6.7 | OV ReacHalfRef | 0 | 61 | % | 0 | 250 | INT | 61
3301 | P 2.17.9.6.8 | OV Max Reactiv | 0 | 61 | % | 0 | 250 | INT | 61
3445 | P 2.17.9.6.9 | OV Reac.Start V | 0 | 62 | % | 0 | 200 | UINT | 62
3501 | P 2.17.9.7.1 | OV Low Corner | 0 | 62 | % | 0 | 320 | INT | 62
3502 | P 2.17.9.7.2 | UV High Corner | 0 | 62 | % | 0 | 320 | INT | 62
3504 | P 2.17.9.7.3 | PosSeqSlope | 2 | 62 | %/% | 0 | 10 | INT | 62
3505 | P 2.17.9.7.4 | NegSeqSlope | 2 | 62 | %/% | 0 | 10 | INT | 62
3503 | P 2.17.9.7.5 | SlopeMaxReactive | 100 | 61 | % | 0 | 170 | INT | 61
3506 | P 2.17.9.7.6 | SudPosChanLim | 10 | 62 | % | -1 | 20 | INT | 62
3507 | P 2.17.9.7.7 | SudNegChanLim | 10 | 62 | % | -1 | 20 | INT | 62
3508 | P 2.17.9.7.8 | RampZeroTime | 5 | 62 | s | 0 | 60 | UINT | 62
3509 | P 2.17.9.7.9 | ResetHysteresis | 1.5 | 62 | % | -10 | 10 | INT | 62
3510 | P 2.17.9.7.10 | SuddebOffDelay | 5 | 63 | s | 0 | 32 | INT | 63
3341 | P 2.17.10.1.1 | HighMax Q Power | 0 | 61 | % | -300 | 300 | INT | 61
3340 | P 2.17.10.1.2 | HighMaxVoltage | 115 | 62 | % | 0 | 200 | INT | 62
3339 | P 2.17.10.1.3 | HighMinVoltage | 105 | 62 | % | 0 | 200 | INT | 62
3343 | P 2.17.10.1.4 | LowMaxVoltage | 90 | 62 | % | 0 | 200 | INT | 62
3342 | P 2.17.10.1.5 | LowMinVoltage | 80 | 62 | % | 0 | 200 | INT | 62
3344 | P 2.17.10.1.6 | LowMax Q Power | 0 | 61 | % | -300 | 300 | INT | 61
3385 | P 2.17.10.2.1 | Voltage 01 | 0 | 62 | % | 0 | 320 | INT | 62
3391 | P 2.17.10.2.2 | Q Power 01 | 0 | 61 | % | -300 | 300 | INT | 61
3386 | P 2.17.10.2.3 | Voltage 02 | 0 | 62 | % | 0 | 320 | INT | 62
3392 | P 2.17.10.2.4 | Q Power 02 | 0 | 61 | % | -300 | 300 | INT | 61
3387 | P 2.17.10.2.5 | Voltage 03 | 0 | 62 | % | 0 | 320 | INT | 62
3393 | P 2.17.10.2.6 | Q Power 03 | 0 | 61 | % | -300 | 300 | INT | 61
3388 | P 2.17.10.2.7 | Voltage 04 | 0 | 62 | % | 0 | 320 | INT | 62
3394 | P 2.17.10.2.8 | Q Power 04 | 0 | 61 | % | -300 | 300 | INT | 61
3389 | P 2.17.10.2.9 | Voltage 05 | 0 | 62 | % | 0 | 320 | INT | 62
3395 | P 2.17.10.2.10 | Q Power 05 | 0 | 61 | % | -300 | 300 | INT | 61
3390 | P 2.17.10.2.11 | Voltage 06 | 0 | 62 | % | 0 | 320 | INT | 62
3396 | P 2.17.10.2.12 | Q Power 06 | 0 | 61 | % | -300 | 300 | INT | 61
3520 | P 2.17.10.3.1 | Power 01 | 0 | 61 | % | -300 | 300 | INT | 61
3530 | P 2.17.10.3.2 | QP Power 01 | 0 | 61 | % | -300 | 300 | INT | 61
3521 | P 2.17.10.3.3 | Power 02 | 0 | 61 | % | -300 | 300 | INT | 61
3531 | P 2.17.10.3.4 | QP Power 02 | 0 | 61 | % | -300 | 300 | INT | 61
3522 | P 2.17.10.3.5 | Power 03 | 0 | 61 | % | -300 | 300 | INT | 61
3532 | P 2.17.10.3.6 | QP Power 03 | 0 | 61 | % | -300 | 300 | INT | 61
3523 | P 2.17.10.3.7 | Power 04 | 0 | 61 | % | -300 | 300 | INT | 61
3533 | P 2.17.10.3.8 | QP Power 04 | 0 | 61 | % | -300 | 300 | INT | 61
3524 | P 2.17.10.3.9 | Power 05 | 0 | 61 | % | -300 | 300 | INT | 61
3534 | P 2.17.10.3.10 | QP Power 05 | 0 | 61 | % | -300 | 300 | INT | 61
3525 | P 2.17.10.3.11 | Power 06 | 0 | 61 | % | -300 | 300 | INT | 61
3535 | P 2.17.10.3.12 | QP Power 06 | 0 | 61 | % | -300 | 300 | INT | 61
3526 | P 2.17.10.3.13 | Power 07 | 0 | 61 | % | -300 | 300 | INT | 61
3536 | P 2.17.10.3.14 | QP Power 07 | 0 | 61 | % | -300 | 300 | INT | 61
3527 | P 2.17.10.3.15 | Power 08 | 0 | 61 | % | -300 | 300 | INT | 61
3537 | P 2.17.10.3.16 | QP Power 08 | 0 | 61 | % | -300 | 300 | INT | 61
3528 | P 2.17.10.3.17 | Power 09 | 0 | 61 | % | -300 | 300 | INT | 61
3538 | P 2.17.10.3.18 | QP Power 09 | 0 | 61 | % | -300 | 300 | INT | 61
3529 | P 2.17.10.3.19 | Power 10 | 0 | 61 | % | -300 | 300 | INT | 61
3539 | P 2.17.10.3.20 | QP Power 10 | 0 | 61 | % | -300 | 300 | INT | 61
3324 | P 2.17.11.1.1 | PowerRampUp | 50 | 62 | %/s | -2 | 320 | INT | 62
3397 | P 2.17.11.1.2 | GC Max Power | 105 | 61 | % | 0 | 300 | INT | 61
3439 | P 2.17.11.1.3 | GC Min Power | 105 | 61 | % | 0 | 300 | INT | 61
3449 | P 2.17.11.1.4 | PowerRefRamp | 50 | 62 | %/s | -1 | 320 | INT | 62
3307 | P 2.17.11.2.1 | HighFreqModes | 0 / High Limit |  |  | 0 | 1 | INT
3295 | P 2.17.11.2.2 | HighFreqLowCornr | 0 | 62 | % | 0 | 200 | INT | 62
3239 | P 2.17.11.2.3 | HighFreqPLimSlop | 50 | 61 | %/Hz | -1 | 300 | INT | 61
3308 | P 2.17.11.2.4 | HighFreqLockOut | 0 | 62 | % | 0 | 150 | INT | 62
3298 | P 2.17.11.2.5 | HighFreqPLimRamp | -1 | 62 | %/s | -1 | 320 | INT | 62
3299 | P 2.17.11.2.6 | HighFreqPReleDel | 50 | 100 | ms | 0 | 1000000 | DINT | 100
3374 | P 2.17.11.2.7 | HighLFFullPRelDe | 0 | 100 | ms | 0 | 400000 | DINT | 100
3402 | P 2.17.11.2.8 | HighFreqLimOnDel | 100 | 60 | ms | 0 | 3000 | DINT | 60
3296 | P 2.17.11.2.9 | HighFreqHigCornr | 0 | 62 | % | 0 | 200 | INT | 62
3309 | P 2.17.11.2.10 | HighFreqPowRatio | 0 | 61 | % | 0 | 100 | INT | 61
3360 | P 2.17.11.3.1 | Limit Mode | 0 / High Limit |  |  | 0 | 1 | INT
3325 | P 2.17.11.3.2 | LogInVoltage | 0 | 62 | % | 0 | 320 | INT | 62
3326 | P 2.17.11.3.3 | LogOutVoltage | 0 | 62 | % | 0 | 320 | INT | 62
3327 | P 2.17.11.3.4 | Limit Slope | 0 | 61 | %/% | -10 | 3200 | INT | 61
3424 | P 2.17.11.3.5 | PLimReleaseDelay | 0 | 100 | ms | 0 | 1200000 | DINT | 100
3425 | P 2.17.11.3.6 | PLimRelRampRate | -0.01 | 62 | %/s | -1 | 320 | INT | 62
3347 | P 2.17.11.4.1 | PChargeMaxVolt | 0 | 62 | % | 0 | 200 | INT | 62
3348 | P 2.17.11.4.2 | PChargeMinVolt | 0 | 62 | % | 0 | 200 | INT | 62
3354 | P 2.17.11.5.1 | PChargeLimMode | 1 / Minimum |  |  | 0 | 3 | INT
3349 | P 2.17.11.5.2 | PChargeMaxFreq | 0 | 62 | % | 0 | 200 | INT | 62
3350 | P 2.17.11.5.3 | PChargeMinFreq | 0 | 62 | % | 0 | 200 | INT | 62
3351 | P 2.17.11.5.4 | PChargLogOutFreq | 0 | 62 | % | 0 | 200 | INT | 62
3352 | P 2.17.11.5.5 | PChrgLogOutDelay | 50 | 100 | ms | 0 | 1000000 | DINT | 100
3355 | P 2.17.11.5.6 | PCharRelPRate | 50 | 62 | %/s | -1 | 300 | INT | 62
3403 | P 2.17.11.5.7 | PChargeOnDelay | 50 | 60 | ms | 0 | 3000 | DINT | 60
3334 | P 2.17.12.1.1 | PowIncLogInFreq | 0 | 62 | % | 0 | 200 | INT | 62
3437 | P 2.17.12.1.2 | PowIncLogOffFreq | 0 | 62 | % | 0 | 200 | INT | 62
3335 | P 2.17.12.1.3 | PowerIncSlope | 0 | 61 | %/% | 0 | 200 | INT | 61
3427 | P 2.17.12.1.4 | PowerIncOffRamp | -1 | 62 | %/s | -1 | 320 | INT | 62
3438 | P 2.17.12.1.5 | PowerIncOffDelay | 0 | 103 | s | 0 | 600 | DINT | 103
3336 | P 2.17.12.1.6 | PowerInc Max | 300 | 61 | % | -300 | 300 | INT | 61
3441 | P 2.17.12.1.7 | PowerIncLowFreq | 0 | 62 | % | 0 | 200 | INT | 62
3443 | P 2.17.12.1.8 | PowerIncSetPFreq | 0 | 62 | % | 0 | 200 | INT | 62
3428 | P 2.17.12.2.1 | PowDecLogInFreq | 0 | 62 | % | 0 | 200 | INT | 62
3436 | P 2.17.12.2.2 | PowDecLogOffFreq | 0 | 62 | % | 0 | 200 | INT | 62
3429 | P 2.17.12.2.3 | PowerDecSlope | 0 | 61 | %/% | -3200 | 3200 | INT | 61
3431 | P 2.17.12.2.4 | PowerDecOffRamp | -1 | 62 | %/s | -1 | 320 | INT | 62
3435 | P 2.17.12.2.5 | PowerDecOffDelay | 0 | 103 | s | 0 | 600 | DINT | 103
3430 | P 2.17.12.2.6 | PowerDec Max | -300 | 61 | % | -300 | 300 | INT | 61
3442 | P 2.17.12.2.7 | PowerDecHighFreq | 0 | 62 | % | 0 | 200 | INT | 62
3432 | P 2.17.12.3.1 | HVPrefLowVolt | 0 | 62 | % | 0 | 200 | INT | 62
3433 | P 2.17.12.3.2 | HV Power Ref | 0 | 61 | % | -300 | 300 | INT | 61
3434 | P 2.17.12.3.3 | HV Power Ramp | -1 | 62 | %/s | -1 | 320 | INT | 62
3345 | P 2.17.13.1 | CosPhiiMode | 0 / Direct Ref |  |  | 0 | 3 | INT
3304 | P 2.17.13.2 | CosPhiiRef | 0 | 63 |  | -1 | 1 | INT | 63
3305 | P 2.17.13.3.1 | LockInVoltage | 0 | 62 | % | 0 | 150 | INT | 62
3306 | P 2.17.13.3.2 | LockOutVoltage | 0 | 62 | % | 0 | 150 | INT | 62
3346 | P 2.17.13.3.3 | MaxCosRef | 1 | 63 |  | -1 | 1 | INT | 63
3357 | P 2.17.13.4.1 | MinCosRefMinPowr | 15 | 61 | % | -150 | 150 | INT | 61
3356 | P 2.17.13.4.2 | MinCosRef | 1 | 63 |  | -1 | 1 | INT | 63
3358 | P 2.17.13.4.3 | CosRefMidPower | 50 | 61 | % | -150 | 150 | INT | 61
3359 | P 2.17.13.4.4 | MaxCosRefMaxPowr | 150 | 61 | % | -150 | 150 | INT | 61
3346 | P 2.17.13.4.5 | MaxCosRef | 1 | 63 |  | -1 | 1 | INT | 63
3310 | P 2.17.14.1 | Ext GC Trip NO | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
3398 | P 2.17.14.2 | Ext GC Trip NC | DigIN:0.2 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
3311 | P 2.17.14.3 | SeparateFLimMon | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
3312 | P 2.17.14.4 | SepFreqHighLim | 0 | 62 | % | 0 | 150 | INT | 62
3313 | P 2.17.14.5 | SepFreqLowLim | 0 | 62 | % | 0 | 150 | INT | 62
3446 | P 2.17.15.1 | EnableLimSup | DigIN:0.1 | 1 |  | DigIN:0.1 | DigIN:E.10 | INT | 1
3447 | P 2.17.15.2 | LimitedSuppMode | 1 / Enabled |  |  | 0 | 1 | INT
3448 | P 2.17.15.3 | VoltageLevel | 90 | 62 | % | 0 | 320 | INT | 62
3328 | P 2.17.16.1 | GC Options 1 | 0 | 60 |  | 0 | 65535 | UINT | 60
3332 | P 2.17.16.2 | Voltage Filt TC | 20 | 60 | ms | 0 | 10000 | INT | 60
3333 | P 2.17.16.3 | Frequecy Filt TC | 35 | 60 | ms | 0 | 10000 | INT | 60
3400 | P 2.17.16.4 | FRT Opt | 0 | 60 |  | 0 | 65535 | WORD | 60
3337 | P 2.17.16.5 | Vac Stop Offset | 0 | 62 | % | -10 | 10 | INT | 62
3338 | P 2.17.16.6 | Vac Run Offset | 0 | 62 | % | -10 | 10 | INT | 62
1529 | P 2.17.16.7 | PowerFoll.Hyst. | 3 | 61 | % | 0 | 100 | INT | 61
3373 | P 2.17.16.8 | LVHighFiltTC | 100 | 60 | ms | 0 | 10000 | INT | 60
3375 | P 2.17.16.9 | LineFreqLow TC | 20 | 60 | ms | 0 | 100 | INT | 60
3382 | P 2.17.16.10 | FRT Trig Level | 0 | 62 | % | 0 | 320 | INT | 62
3409 | P 2.17.16.11 | Current x TC | 16 | 60 | ms | 0 | 1000 | INT | 60
3420 | P 2.17.16.12 | LV Feedback Kp | 0 | 62 | % | 0 | 300 | INT | 62
3422 | P 2.17.16.13 | Current Priority | 0 / Normal |  |  | 0 | 4 | INT
3440 | P 2.17.16.14 | LineFreqHigh TC | 120 | 60 | ms | 0 | 3000 | INT | 60
3540 | P 2.17.16.15 | ReactiveVoltComp | 0 / No |  |  | 0 | 1 | INT